## History
History:
Version | Date | Descriptions
0.10 | 2021-01-04 | First release
0.20 | 2021-01-27 | With SNMP 0.30 a15
0.30 | 2021-03-04 | Fixed the INLET leakage current unit
0.40 | 2021-04-27 | Fixed the EMD humidity, inlet/outlet energy and current unit, OUTLET closing delay time
0.50 | 2021-11-03 | Add PF alarm
0.60 | 2022-01-12 | Add Power Share
0.70 | 2022-01-27 | Modify Power Share.
0.80 | 2022-03-22 | Fixed the address problem.
0.90 | 2023-01-18 | Add Outlet Sequential Startup Configuration Remove Off Delay Time Status and On Delay Time Status
1.00 | 2023-02-24 | Intlet/Outlet Power Factor unit cnahge 0.1 to 0.01
2.00 | 2025-03-03 | 1. Increase outlet ports from 42 to 48 2.Add inlet RW 4 bytes for Inlet Over Load Warning and Inlet Over Load Critical

## 0x03 Holdings
PDU Address (DEC) | Parameter Name | Access | Size | Remark
0 | Master Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1 | Slave01 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
2 | Slave02 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
3 | Slave03 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
4 | Slave04 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5 | Slave05 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
6 | Slave06 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
7 | Slave07 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
8 | Slave08 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
9 | Slave09 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
10 | Slave10 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
11 | Slave11 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
12 | Slave12 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
13 | Slave13 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
14 | Slave14 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
15 | Slave15 Inlet Valid | RO | 2 bytes | 1:Valid; 0:Invalid
16 | Master Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
17 | Slave01 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
18 | Slave02 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
19 | Slave03 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
20 | Slave04 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
21 | Slave05 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
22 | Slave06 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
23 | Slave07 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
24 | Slave08 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
25 | Slave09 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
26 | Slave10 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
27 | Slave11 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
28 | Slave12 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
29 | Slave13 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
30 | Slave14 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
31 | Slave15 Inlet Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1]; Bit10:CT Channel. 1CH[0]/2CH[1]; Bit11:Current Breaker. 16A[0]/32A[1];Bit15:A2 Format Bitmap; must is 1
32 | Master Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
33 | Slave01 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
34 | Slave02 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
35 | Slave03 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
36 | Slave04 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
37 | Slave05 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
38 | Slave06 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
39 | Slave07 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
40 | Slave08 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
41 | Slave09 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
42 | Slave10 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
43 | Slave11 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
44 | Slave12 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
45 | Slave13 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
46 | Slave14 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
47 | Slave15 Inlet Over Load Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
48 | Master Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
49 | Slave01 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
50 | Slave02 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
51 | Slave03 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
52 | Slave04 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
53 | Slave05 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
54 | Slave06 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
55 | Slave07 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
56 | Slave08 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
57 | Slave09 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
58 | Slave10 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
59 | Slave11 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
60 | Slave12 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
61 | Slave13 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
62 | Slave14 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
63 | Slave15 Inlet Phase1 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
64 | Master Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
65 | Slave01 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
66 | Slave02 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
67 | Slave03 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
68 | Slave04 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
69 | Slave05 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
70 | Slave06 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
71 | Slave07 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
72 | Slave08 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
73 | Slave09 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
74 | Slave10 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
75 | Slave11 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
76 | Slave12 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
77 | Slave13 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
78 | Slave14 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
79 | Slave15 Inlet Phase2 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
80 | Master Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
81 | Slave01 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
82 | Slave02 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
83 | Slave03 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
84 | Slave04 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
85 | Slave05 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
86 | Slave06 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
87 | Slave07 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
88 | Slave08 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
89 | Slave09 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
90 | Slave10 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
91 | Slave11 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
92 | Slave12 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
93 | Slave13 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
94 | Slave14 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
95 | Slave15 Inlet Phase3 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Branch1 Over Current Warning;Bit3:Branch1 Over Current Critical;Bit4:Branch1 Over Voltage Warning;Bit5:Branch1 Over Voltage Critical;Bit6:Branch2 Over Current Warning;Bit7:Branch2 Over Current Critical;Bit8:Total Over Current Warning;Bit9:Total Over Current Critical;Bit10:Branch1 Over PF Warning;Bit11:Branch1 Over PF Critical;Bit12:Branch2 Over PF Warning;Bit13:Branch2 Over PF Critical
96 | Master Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
97 | Slave01 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
98 | Slave02 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
99 | Slave03 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
100 | Slave04 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
101 | Slave05 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
102 | Slave06 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
103 | Slave07 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
104 | Slave08 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
105 | Slave09 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
106 | Slave10 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
107 | Slave11 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
108 | Slave12 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
109 | Slave13 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
110 | Slave14 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
111 | Slave15 Inlet Balance Status | RO | 2 bytes | Bit0:Warning; Bit1:Critical
112 | Master Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
113 | Slave01 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
114 | Slave02 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
115 | Slave03 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
116 | Slave04 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
117 | Slave05 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
118 | Slave06 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
119 | Slave07 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
120 | Slave08 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
121 | Slave09 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
122 | Slave10 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
123 | Slave11 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
124 | Slave12 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
125 | Slave13 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
126 | Slave14 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
127 | Slave15 Inlet Phase1 Voltage | RO | 2 bytes | Unit:0.1
128 | Master Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
129 | Slave01 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
130 | Slave02 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
131 | Slave03 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
132 | Slave04 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
133 | Slave05 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
134 | Slave06 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
135 | Slave07 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
136 | Slave08 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
137 | Slave09 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
138 | Slave10 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
139 | Slave11 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
140 | Slave12 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
141 | Slave13 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
142 | Slave14 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
143 | Slave15 Inlet Phase2 Voltage | RO | 2 bytes | Unit:0.1
144 | Master Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
145 | Slave01 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
146 | Slave02 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
147 | Slave03 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
148 | Slave04 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
149 | Slave05 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
150 | Slave06 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
151 | Slave07 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
152 | Slave08 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
153 | Slave09 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
154 | Slave10 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
155 | Slave11 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
156 | Slave12 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
157 | Slave13 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
158 | Slave14 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
159 | Slave15 Inlet Phase3 Voltage | RO | 2 bytes | Unit:0.1
160 | Master Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
161 | Slave01 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
162 | Slave02 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
163 | Slave03 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
164 | Slave04 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
165 | Slave05 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
166 | Slave06 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
167 | Slave07 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
168 | Slave08 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
169 | Slave09 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
170 | Slave10 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
171 | Slave11 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
172 | Slave12 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
173 | Slave13 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
174 | Slave14 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
175 | Slave15 Inlet Phase1 Frequency | RO | 2 bytes | Unit:0.01
176 | Master Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
177 | Slave01 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
178 | Slave02 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
179 | Slave03 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
180 | Slave04 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
181 | Slave05 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
182 | Slave06 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
183 | Slave07 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
184 | Slave08 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
185 | Slave09 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
186 | Slave10 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
187 | Slave11 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
188 | Slave12 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
189 | Slave13 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
190 | Slave14 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
191 | Slave15 Inlet Phase2 Frequency | RO | 2 bytes | Unit:0.01
192 | Master Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
193 | Slave01 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
194 | Slave02 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
195 | Slave03 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
196 | Slave04 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
197 | Slave05 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
198 | Slave06 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
199 | Slave07 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
200 | Slave08 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
201 | Slave09 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
202 | Slave10 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
203 | Slave11 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
204 | Slave12 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
205 | Slave13 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
206 | Slave14 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
207 | Slave15 Inlet Phase3 Frequency | RO | 2 bytes | Unit:0.01
208 | Master Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
209 | Slave01 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
210 | Slave02 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
211 | Slave03 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
212 | Slave04 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
213 | Slave05 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
214 | Slave06 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
215 | Slave07 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
216 | Slave08 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
217 | Slave09 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
218 | Slave10 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
219 | Slave11 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
220 | Slave12 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
221 | Slave13 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
222 | Slave14 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
223 | Slave15 Inlet Phase1 PF for Branch1 | RO | 2 bytes | Unit:0.01
224 | Master Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
225 | Slave01 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
226 | Slave02 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
227 | Slave03 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
228 | Slave04 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
229 | Slave05 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
230 | Slave06 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
231 | Slave07 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
232 | Slave08 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
233 | Slave09 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
234 | Slave10 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
235 | Slave11 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
236 | Slave12 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
237 | Slave13 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
238 | Slave14 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
239 | Slave15 Inlet Phase2 PF for Branch1 | RO | 2 bytes | Unit:0.01
240 | Master Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
241 | Slave01 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
242 | Slave02 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
243 | Slave03 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
244 | Slave04 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
245 | Slave05 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
246 | Slave06 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
247 | Slave07 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
248 | Slave08 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
249 | Slave09 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
250 | Slave10 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
251 | Slave11 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
252 | Slave12 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
253 | Slave13 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
254 | Slave14 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
255 | Slave15 Inlet Phase3 PF for Branch1 | RO | 2 bytes | Unit:0.01
256 | Master Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
257 | Slave01 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
258 | Slave02 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
259 | Slave03 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
260 | Slave04 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
261 | Slave05 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
262 | Slave06 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
263 | Slave07 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
264 | Slave08 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
265 | Slave09 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
266 | Slave10 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
267 | Slave11 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
268 | Slave12 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
269 | Slave13 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
270 | Slave14 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
271 | Slave15 Inlet Phase1 PF for Branch2 | RO | 2 bytes | Unit:0.01
272 | Master Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
273 | Slave01 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
274 | Slave02 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
275 | Slave03 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
276 | Slave04 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
277 | Slave05 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
278 | Slave06 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
279 | Slave07 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
280 | Slave08 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
281 | Slave09 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
282 | Slave10 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
283 | Slave11 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
284 | Slave12 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
285 | Slave13 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
286 | Slave14 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
287 | Slave15 Inlet Phase2 PF for Branch2 | RO | 2 bytes | Unit:0.01
288 | Master Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
289 | Slave01 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
290 | Slave02 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
291 | Slave03 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
292 | Slave04 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
293 | Slave05 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
294 | Slave06 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
295 | Slave07 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
296 | Slave08 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
297 | Slave09 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
298 | Slave10 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
299 | Slave11 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
300 | Slave12 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
301 | Slave13 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
302 | Slave14 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
303 | Slave15 Inlet Phase3 PF for Branch2 | RO | 2 bytes | Unit:0.01
304 | Master Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
305 | Slave01 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
306 | Slave02 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
307 | Slave03 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
308 | Slave04 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
309 | Slave05 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
310 | Slave06 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
311 | Slave07 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
312 | Slave08 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
313 | Slave09 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
314 | Slave10 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
315 | Slave11 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
316 | Slave12 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
317 | Slave13 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
318 | Slave14 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
319 | Slave15 Inlet Phase1 Current for Branch1 | RO | 2 bytes | Unit:0.01
320 | Master Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
321 | Slave01 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
322 | Slave02 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
323 | Slave03 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
324 | Slave04 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
325 | Slave05 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
326 | Slave06 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
327 | Slave07 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
328 | Slave08 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
329 | Slave09 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
330 | Slave10 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
331 | Slave11 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
332 | Slave12 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
333 | Slave13 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
334 | Slave14 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
335 | Slave15 Inlet Phase2 Current for Branch1 | RO | 2 bytes | Unit:0.01
336 | Master Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
337 | Slave01 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
338 | Slave02 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
339 | Slave03 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
340 | Slave04 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
341 | Slave05 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
342 | Slave06 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
343 | Slave07 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
344 | Slave08 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
345 | Slave09 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
346 | Slave10 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
347 | Slave11 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
348 | Slave12 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
349 | Slave13 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
350 | Slave14 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
351 | Slave15 Inlet Phase3 Current for Branch1 | RO | 2 bytes | Unit:0.01
352 | Master Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
353 | Slave01 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
354 | Slave02 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
355 | Slave03 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
356 | Slave04 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
357 | Slave05 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
358 | Slave06 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
359 | Slave07 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
360 | Slave08 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
361 | Slave09 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
362 | Slave10 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
363 | Slave11 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
364 | Slave12 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
365 | Slave13 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
366 | Slave14 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
367 | Slave15 Inlet Phase1 Current for Branch2 | RO | 2 bytes | Unit:0.01
368 | Master Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
369 | Slave01 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
370 | Slave02 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
371 | Slave03 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
372 | Slave04 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
373 | Slave05 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
374 | Slave06 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
375 | Slave07 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
376 | Slave08 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
377 | Slave09 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
378 | Slave10 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
379 | Slave11 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
380 | Slave12 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
381 | Slave13 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
382 | Slave14 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
383 | Slave15 Inlet Phase2 Current for Branch2 | RO | 2 bytes | Unit:0.01
384 | Master Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
385 | Slave01 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
386 | Slave02 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
387 | Slave03 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
388 | Slave04 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
389 | Slave05 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
390 | Slave06 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
391 | Slave07 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
392 | Slave08 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
393 | Slave09 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
394 | Slave10 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
395 | Slave11 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
396 | Slave12 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
397 | Slave13 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
398 | Slave14 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
399 | Slave15 Inlet Phase3 Current for Branch2 | RO | 2 bytes | Unit:0.01
400 | Master Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
401 | Slave01 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
402 | Slave02 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
403 | Slave03 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
404 | Slave04 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
405 | Slave05 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
406 | Slave06 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
407 | Slave07 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
408 | Slave08 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
409 | Slave09 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
410 | Slave10 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
411 | Slave11 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
412 | Slave12 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
413 | Slave13 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
414 | Slave14 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
415 | Slave15 Inlet Leakage Current Valid | RO | 2 bytes | 1:Valid; 0:Invalid
416 | Master Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
417 | Slave01 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
418 | Slave02 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
419 | Slave03 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
420 | Slave04 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
421 | Slave05 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
422 | Slave06 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
423 | Slave07 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
424 | Slave08 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
425 | Slave09 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
426 | Slave10 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
427 | Slave11 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
428 | Slave12 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
429 | Slave13 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
430 | Slave14 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
431 | Slave15 Inlet Leakage Current Value | RO | 2 bytes | Unit:0.1mA
432 | Master Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
433 | Slave01 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
434 | Slave02 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
435 | Slave03 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
436 | Slave04 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
437 | Slave05 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
438 | Slave06 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
439 | Slave07 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
440 | Slave08 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
441 | Slave09 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
442 | Slave10 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
443 | Slave11 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
444 | Slave12 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
445 | Slave13 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
446 | Slave14 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
447 | Slave15 Inlet Leakage Current Status | RO | 2 bytes | 0:normal; 1:alarm
448 | Master Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
449 | Slave01 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
450 | Slave02 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
451 | Slave03 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
452 | Slave04 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
453 | Slave05 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
454 | Slave06 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
455 | Slave07 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
456 | Slave08 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
457 | Slave09 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
458 | Slave10 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
459 | Slave11 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
460 | Slave12 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
461 | Slave13 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
462 | Slave14 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
463 | Slave15 Inlet Power Share Status | RO | 2 bytes | 0:invalid; 1:Inactive; 2:Active/Backup Power; 3:Active/Main Power
464 | Master Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
465 | Master Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
466 | Master Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
467 | Master Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
468 | Master Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
469 | Master Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
470 | Master Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
471 | Master Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
472 | Master Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
473 | Master Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
474 | Master Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
475 | Master Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
476 | Master Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
477 | Master Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
478 | Master Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
479 | Master Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
480 | Master Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
481 | Master Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
482 | Master Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
483 | Master Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
484 | Master Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
485 | Master Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
486 | Master Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
487 | Master Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
488 | Master Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
489 | Master Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
490 | Master Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
491 | Master Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
492 | Master Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
493 | Master Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
494 | Master Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
495 | Master Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
496 | Master Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
497 | Master Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
498 | Master Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
499 | Master Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
500 | Master Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
501 | Master Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
502 | Master Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
503 | Master Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
504 | Master Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
505 | Master Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
506 | Master Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
507 | Master Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
508 | Master Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
509 | Master Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
510 | Master Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
511 | Master Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
512 | Slave01 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
513 | Slave01 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
514 | Slave01 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
515 | Slave01 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
516 | Slave01 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
517 | Slave01 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
518 | Slave01 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
519 | Slave01 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
520 | Slave01 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
521 | Slave01 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
522 | Slave01 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
523 | Slave01 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
524 | Slave01 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
525 | Slave01 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
526 | Slave01 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
527 | Slave01 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
528 | Slave01 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
529 | Slave01 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
530 | Slave01 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
531 | Slave01 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
532 | Slave01 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
533 | Slave01 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
534 | Slave01 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
535 | Slave01 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
536 | Slave01 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
537 | Slave01 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
538 | Slave01 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
539 | Slave01 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
540 | Slave01 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
541 | Slave01 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
542 | Slave01 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
543 | Slave01 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
544 | Slave01 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
545 | Slave01 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
546 | Slave01 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
547 | Slave01 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
548 | Slave01 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
549 | Slave01 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
550 | Slave01 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
551 | Slave01 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
552 | Slave01 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
553 | Slave01 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
554 | Slave01 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
555 | Slave01 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
556 | Slave01 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
557 | Slave01 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
558 | Slave01 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
559 | Slave01 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
560 | Slave02 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
561 | Slave02 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
562 | Slave02 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
563 | Slave02 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
564 | Slave02 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
565 | Slave02 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
566 | Slave02 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
567 | Slave02 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
568 | Slave02 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
569 | Slave02 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
570 | Slave02 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
571 | Slave02 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
572 | Slave02 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
573 | Slave02 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
574 | Slave02 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
575 | Slave02 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
576 | Slave02 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
577 | Slave02 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
578 | Slave02 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
579 | Slave02 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
580 | Slave02 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
581 | Slave02 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
582 | Slave02 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
583 | Slave02 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
584 | Slave02 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
585 | Slave02 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
586 | Slave02 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
587 | Slave02 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
588 | Slave02 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
589 | Slave02 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
590 | Slave02 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
591 | Slave02 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
592 | Slave02 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
593 | Slave02 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
594 | Slave02 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
595 | Slave02 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
596 | Slave02 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
597 | Slave02 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
598 | Slave02 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
599 | Slave02 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
600 | Slave02 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
601 | Slave02 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
602 | Slave02 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
603 | Slave02 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
604 | Slave02 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
605 | Slave02 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
606 | Slave02 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
607 | Slave02 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
608 | Slave03 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
609 | Slave03 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
610 | Slave03 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
611 | Slave03 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
612 | Slave03 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
613 | Slave03 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
614 | Slave03 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
615 | Slave03 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
616 | Slave03 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
617 | Slave03 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
618 | Slave03 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
619 | Slave03 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
620 | Slave03 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
621 | Slave03 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
622 | Slave03 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
623 | Slave03 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
624 | Slave03 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
625 | Slave03 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
626 | Slave03 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
627 | Slave03 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
628 | Slave03 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
629 | Slave03 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
630 | Slave03 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
631 | Slave03 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
632 | Slave03 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
633 | Slave03 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
634 | Slave03 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
635 | Slave03 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
636 | Slave03 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
637 | Slave03 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
638 | Slave03 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
639 | Slave03 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
640 | Slave03 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
641 | Slave03 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
642 | Slave03 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
643 | Slave03 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
644 | Slave03 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
645 | Slave03 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
646 | Slave03 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
647 | Slave03 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
648 | Slave03 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
649 | Slave03 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
650 | Slave03 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
651 | Slave03 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
652 | Slave03 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
653 | Slave03 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
654 | Slave03 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
655 | Slave03 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
656 | Slave04 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
657 | Slave04 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
658 | Slave04 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
659 | Slave04 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
660 | Slave04 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
661 | Slave04 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
662 | Slave04 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
663 | Slave04 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
664 | Slave04 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
665 | Slave04 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
666 | Slave04 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
667 | Slave04 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
668 | Slave04 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
669 | Slave04 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
670 | Slave04 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
671 | Slave04 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
672 | Slave04 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
673 | Slave04 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
674 | Slave04 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
675 | Slave04 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
676 | Slave04 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
677 | Slave04 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
678 | Slave04 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
679 | Slave04 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
680 | Slave04 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
681 | Slave04 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
682 | Slave04 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
683 | Slave04 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
684 | Slave04 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
685 | Slave04 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
686 | Slave04 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
687 | Slave04 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
688 | Slave04 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
689 | Slave04 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
690 | Slave04 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
691 | Slave04 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
692 | Slave04 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
693 | Slave04 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
694 | Slave04 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
695 | Slave04 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
696 | Slave04 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
697 | Slave04 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
698 | Slave04 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
699 | Slave04 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
700 | Slave04 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
701 | Slave04 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
702 | Slave04 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
703 | Slave04 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
704 | Slave05 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
705 | Slave05 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
706 | Slave05 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
707 | Slave05 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
708 | Slave05 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
709 | Slave05 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
710 | Slave05 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
711 | Slave05 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
712 | Slave05 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
713 | Slave05 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
714 | Slave05 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
715 | Slave05 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
716 | Slave05 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
717 | Slave05 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
718 | Slave05 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
719 | Slave05 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
720 | Slave05 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
721 | Slave05 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
722 | Slave05 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
723 | Slave05 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
724 | Slave05 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
725 | Slave05 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
726 | Slave05 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
727 | Slave05 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
728 | Slave05 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
729 | Slave05 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
730 | Slave05 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
731 | Slave05 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
732 | Slave05 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
733 | Slave05 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
734 | Slave05 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
735 | Slave05 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
736 | Slave05 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
737 | Slave05 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
738 | Slave05 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
739 | Slave05 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
740 | Slave05 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
741 | Slave05 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
742 | Slave05 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
743 | Slave05 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
744 | Slave05 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
745 | Slave05 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
746 | Slave05 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
747 | Slave05 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
748 | Slave05 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
749 | Slave05 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
750 | Slave05 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
751 | Slave05 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
752 | Slave06 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
753 | Slave06 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
754 | Slave06 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
755 | Slave06 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
756 | Slave06 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
757 | Slave06 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
758 | Slave06 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
759 | Slave06 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
760 | Slave06 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
761 | Slave06 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
762 | Slave06 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
763 | Slave06 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
764 | Slave06 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
765 | Slave06 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
766 | Slave06 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
767 | Slave06 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
768 | Slave06 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
769 | Slave06 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
770 | Slave06 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
771 | Slave06 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
772 | Slave06 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
773 | Slave06 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
774 | Slave06 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
775 | Slave06 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
776 | Slave06 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
777 | Slave06 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
778 | Slave06 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
779 | Slave06 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
780 | Slave06 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
781 | Slave06 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
782 | Slave06 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
783 | Slave06 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
784 | Slave06 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
785 | Slave06 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
786 | Slave06 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
787 | Slave06 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
788 | Slave06 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
789 | Slave06 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
790 | Slave06 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
791 | Slave06 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
792 | Slave06 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
793 | Slave06 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
794 | Slave06 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
795 | Slave06 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
796 | Slave06 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
797 | Slave06 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
798 | Slave06 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
799 | Slave06 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
800 | Slave07 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
801 | Slave07 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
802 | Slave07 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
803 | Slave07 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
804 | Slave07 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
805 | Slave07 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
806 | Slave07 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
807 | Slave07 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
808 | Slave07 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
809 | Slave07 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
810 | Slave07 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
811 | Slave07 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
812 | Slave07 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
813 | Slave07 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
814 | Slave07 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
815 | Slave07 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
816 | Slave07 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
817 | Slave07 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
818 | Slave07 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
819 | Slave07 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
820 | Slave07 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
821 | Slave07 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
822 | Slave07 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
823 | Slave07 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
824 | Slave07 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
825 | Slave07 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
826 | Slave07 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
827 | Slave07 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
828 | Slave07 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
829 | Slave07 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
830 | Slave07 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
831 | Slave07 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
832 | Slave07 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
833 | Slave07 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
834 | Slave07 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
835 | Slave07 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
836 | Slave07 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
837 | Slave07 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
838 | Slave07 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
839 | Slave07 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
840 | Slave07 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
841 | Slave07 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
842 | Slave07 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
843 | Slave07 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
844 | Slave07 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
845 | Slave07 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
846 | Slave07 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
847 | Slave07 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
848 | Slave08 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
849 | Slave08 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
850 | Slave08 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
851 | Slave08 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
852 | Slave08 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
853 | Slave08 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
854 | Slave08 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
855 | Slave08 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
856 | Slave08 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
857 | Slave08 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
858 | Slave08 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
859 | Slave08 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
860 | Slave08 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
861 | Slave08 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
862 | Slave08 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
863 | Slave08 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
864 | Slave08 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
865 | Slave08 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
866 | Slave08 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
867 | Slave08 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
868 | Slave08 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
869 | Slave08 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
870 | Slave08 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
871 | Slave08 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
872 | Slave08 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
873 | Slave08 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
874 | Slave08 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
875 | Slave08 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
876 | Slave08 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
877 | Slave08 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
878 | Slave08 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
879 | Slave08 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
880 | Slave08 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
881 | Slave08 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
882 | Slave08 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
883 | Slave08 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
884 | Slave08 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
885 | Slave08 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
886 | Slave08 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
887 | Slave08 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
888 | Slave08 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
889 | Slave08 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
890 | Slave08 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
891 | Slave08 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
892 | Slave08 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
893 | Slave08 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
894 | Slave08 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
895 | Slave08 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
896 | Slave09 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
897 | Slave09 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
898 | Slave09 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
899 | Slave09 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
900 | Slave09 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
901 | Slave09 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
902 | Slave09 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
903 | Slave09 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
904 | Slave09 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
905 | Slave09 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
906 | Slave09 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
907 | Slave09 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
908 | Slave09 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
909 | Slave09 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
910 | Slave09 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
911 | Slave09 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
912 | Slave09 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
913 | Slave09 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
914 | Slave09 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
915 | Slave09 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
916 | Slave09 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
917 | Slave09 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
918 | Slave09 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
919 | Slave09 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
920 | Slave09 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
921 | Slave09 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
922 | Slave09 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
923 | Slave09 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
924 | Slave09 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
925 | Slave09 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
926 | Slave09 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
927 | Slave09 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
928 | Slave09 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
929 | Slave09 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
930 | Slave09 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
931 | Slave09 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
932 | Slave09 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
933 | Slave09 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
934 | Slave09 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
935 | Slave09 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
936 | Slave09 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
937 | Slave09 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
938 | Slave09 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
939 | Slave09 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
940 | Slave09 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
941 | Slave09 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
942 | Slave09 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
943 | Slave09 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
944 | Slave10 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
945 | Slave10 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
946 | Slave10 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
947 | Slave10 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
948 | Slave10 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
949 | Slave10 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
950 | Slave10 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
951 | Slave10 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
952 | Slave10 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
953 | Slave10 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
954 | Slave10 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
955 | Slave10 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
956 | Slave10 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
957 | Slave10 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
958 | Slave10 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
959 | Slave10 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
960 | Slave10 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
961 | Slave10 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
962 | Slave10 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
963 | Slave10 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
964 | Slave10 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
965 | Slave10 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
966 | Slave10 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
967 | Slave10 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
968 | Slave10 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
969 | Slave10 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
970 | Slave10 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
971 | Slave10 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
972 | Slave10 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
973 | Slave10 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
974 | Slave10 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
975 | Slave10 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
976 | Slave10 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
977 | Slave10 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
978 | Slave10 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
979 | Slave10 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
980 | Slave10 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
981 | Slave10 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
982 | Slave10 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
983 | Slave10 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
984 | Slave10 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
985 | Slave10 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
986 | Slave10 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
987 | Slave10 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
988 | Slave10 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
989 | Slave10 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
990 | Slave10 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
991 | Slave10 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
992 | Slave11 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
993 | Slave11 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
994 | Slave11 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
995 | Slave11 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
996 | Slave11 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
997 | Slave11 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
998 | Slave11 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
999 | Slave11 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1000 | Slave11 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1001 | Slave11 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1002 | Slave11 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1003 | Slave11 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1004 | Slave11 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1005 | Slave11 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1006 | Slave11 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1007 | Slave11 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1008 | Slave11 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1009 | Slave11 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1010 | Slave11 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1011 | Slave11 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1012 | Slave11 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1013 | Slave11 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1014 | Slave11 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1015 | Slave11 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1016 | Slave11 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1017 | Slave11 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1018 | Slave11 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1019 | Slave11 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1020 | Slave11 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1021 | Slave11 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1022 | Slave11 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1023 | Slave11 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1024 | Slave11 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1025 | Slave11 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1026 | Slave11 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1027 | Slave11 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1028 | Slave11 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1029 | Slave11 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1030 | Slave11 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1031 | Slave11 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1032 | Slave11 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1033 | Slave11 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1034 | Slave11 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1035 | Slave11 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1036 | Slave11 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1037 | Slave11 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1038 | Slave11 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1039 | Slave11 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1040 | Slave12 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1041 | Slave12 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1042 | Slave12 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1043 | Slave12 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1044 | Slave12 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1045 | Slave12 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1046 | Slave12 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1047 | Slave12 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1048 | Slave12 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1049 | Slave12 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1050 | Slave12 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1051 | Slave12 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1052 | Slave12 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1053 | Slave12 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1054 | Slave12 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1055 | Slave12 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1056 | Slave12 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1057 | Slave12 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1058 | Slave12 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1059 | Slave12 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1060 | Slave12 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1061 | Slave12 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1062 | Slave12 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1063 | Slave12 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1064 | Slave12 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1065 | Slave12 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1066 | Slave12 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1067 | Slave12 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1068 | Slave12 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1069 | Slave12 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1070 | Slave12 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1071 | Slave12 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1072 | Slave12 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1073 | Slave12 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1074 | Slave12 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1075 | Slave12 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1076 | Slave12 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1077 | Slave12 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1078 | Slave12 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1079 | Slave12 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1080 | Slave12 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1081 | Slave12 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1082 | Slave12 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1083 | Slave12 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1084 | Slave12 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1085 | Slave12 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1086 | Slave12 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1087 | Slave12 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1088 | Slave13 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1089 | Slave13 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1090 | Slave13 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1091 | Slave13 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1092 | Slave13 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1093 | Slave13 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1094 | Slave13 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1095 | Slave13 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1096 | Slave13 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1097 | Slave13 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1098 | Slave13 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1099 | Slave13 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1100 | Slave13 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1101 | Slave13 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1102 | Slave13 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1103 | Slave13 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1104 | Slave13 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1105 | Slave13 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1106 | Slave13 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1107 | Slave13 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1108 | Slave13 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1109 | Slave13 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1110 | Slave13 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1111 | Slave13 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1112 | Slave13 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1113 | Slave13 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1114 | Slave13 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1115 | Slave13 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1116 | Slave13 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1117 | Slave13 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1118 | Slave13 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1119 | Slave13 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1120 | Slave13 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1121 | Slave13 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1122 | Slave13 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1123 | Slave13 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1124 | Slave13 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1125 | Slave13 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1126 | Slave13 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1127 | Slave13 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1128 | Slave13 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1129 | Slave13 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1130 | Slave13 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1131 | Slave13 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1132 | Slave13 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1133 | Slave13 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1134 | Slave13 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1135 | Slave13 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1136 | Slave14 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1137 | Slave14 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1138 | Slave14 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1139 | Slave14 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1140 | Slave14 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1141 | Slave14 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1142 | Slave14 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1143 | Slave14 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1144 | Slave14 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1145 | Slave14 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1146 | Slave14 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1147 | Slave14 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1148 | Slave14 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1149 | Slave14 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1150 | Slave14 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1151 | Slave14 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1152 | Slave14 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1153 | Slave14 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1154 | Slave14 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1155 | Slave14 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1156 | Slave14 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1157 | Slave14 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1158 | Slave14 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1159 | Slave14 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1160 | Slave14 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1161 | Slave14 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1162 | Slave14 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1163 | Slave14 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1164 | Slave14 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1165 | Slave14 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1166 | Slave14 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1167 | Slave14 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1168 | Slave14 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1169 | Slave14 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1170 | Slave14 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1171 | Slave14 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1172 | Slave14 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1173 | Slave14 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1174 | Slave14 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1175 | Slave14 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1176 | Slave14 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1177 | Slave14 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1178 | Slave14 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1179 | Slave14 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1180 | Slave14 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1181 | Slave14 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1182 | Slave14 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1183 | Slave14 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1184 | Slave15 Outlet Port01 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1185 | Slave15 Outlet Port02 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1186 | Slave15 Outlet Port03 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1187 | Slave15 Outlet Port04 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1188 | Slave15 Outlet Port05 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1189 | Slave15 Outlet Port06 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1190 | Slave15 Outlet Port07 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1191 | Slave15 Outlet Port08 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1192 | Slave15 Outlet Port09 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1193 | Slave15 Outlet Port10 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1194 | Slave15 Outlet Port11 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1195 | Slave15 Outlet Port12 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1196 | Slave15 Outlet Port13 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1197 | Slave15 Outlet Port14 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1198 | Slave15 Outlet Port15 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1199 | Slave15 Outlet Port16 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1200 | Slave15 Outlet Port17 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1201 | Slave15 Outlet Port18 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1202 | Slave15 Outlet Port19 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1203 | Slave15 Outlet Port20 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1204 | Slave15 Outlet Port21 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1205 | Slave15 Outlet Port22 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1206 | Slave15 Outlet Port23 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1207 | Slave15 Outlet Port24 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1208 | Slave15 Outlet Port25 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1209 | Slave15 Outlet Port26 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1210 | Slave15 Outlet Port27 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1211 | Slave15 Outlet Port28 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1212 | Slave15 Outlet Port29 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1213 | Slave15 Outlet Port30 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1214 | Slave15 Outlet Port31 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1215 | Slave15 Outlet Port32 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1216 | Slave15 Outlet Port33 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1217 | Slave15 Outlet Port34 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1218 | Slave15 Outlet Port35 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1219 | Slave15 Outlet Port36 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1220 | Slave15 Outlet Port37 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1221 | Slave15 Outlet Port38 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1222 | Slave15 Outlet Port39 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1223 | Slave15 Outlet Port40 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1224 | Slave15 Outlet Port41 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1225 | Slave15 Outlet Port42 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1226 | Slave15 Outlet Port43 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1227 | Slave15 Outlet Port44 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1228 | Slave15 Outlet Port45 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1229 | Slave15 Outlet Port46 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1230 | Slave15 Outlet Port47 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1231 | Slave15 Outlet Port48 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
1232 | Master Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1233 | Master Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1234 | Master Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1235 | Master Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1236 | Master Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1237 | Master Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1238 | Master Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1239 | Master Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1240 | Master Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1241 | Master Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1242 | Master Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1243 | Master Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1244 | Master Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1245 | Master Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1246 | Master Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1247 | Master Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1248 | Master Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1249 | Master Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1250 | Master Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1251 | Master Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1252 | Master Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1253 | Master Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1254 | Master Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1255 | Master Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1256 | Master Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1257 | Master Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1258 | Master Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1259 | Master Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1260 | Master Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1261 | Master Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1262 | Master Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1263 | Master Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1264 | Master Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1265 | Master Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1266 | Master Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1267 | Master Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1268 | Master Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1269 | Master Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1270 | Master Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1271 | Master Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1272 | Master Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1273 | Master Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1274 | Master Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1275 | Master Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1276 | Master Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1277 | Master Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1278 | Master Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1279 | Master Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1280 | Slave01 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1281 | Slave01 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1282 | Slave01 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1283 | Slave01 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1284 | Slave01 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1285 | Slave01 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1286 | Slave01 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1287 | Slave01 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1288 | Slave01 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1289 | Slave01 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1290 | Slave01 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1291 | Slave01 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1292 | Slave01 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1293 | Slave01 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1294 | Slave01 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1295 | Slave01 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1296 | Slave01 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1297 | Slave01 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1298 | Slave01 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1299 | Slave01 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1300 | Slave01 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1301 | Slave01 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1302 | Slave01 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1303 | Slave01 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1304 | Slave01 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1305 | Slave01 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1306 | Slave01 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1307 | Slave01 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1308 | Slave01 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1309 | Slave01 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1310 | Slave01 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1311 | Slave01 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1312 | Slave01 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1313 | Slave01 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1314 | Slave01 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1315 | Slave01 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1316 | Slave01 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1317 | Slave01 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1318 | Slave01 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1319 | Slave01 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1320 | Slave01 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1321 | Slave01 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1322 | Slave01 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1323 | Slave01 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1324 | Slave01 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1325 | Slave01 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1326 | Slave01 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1327 | Slave01 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1328 | Slave02 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1329 | Slave02 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1330 | Slave02 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1331 | Slave02 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1332 | Slave02 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1333 | Slave02 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1334 | Slave02 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1335 | Slave02 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1336 | Slave02 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1337 | Slave02 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1338 | Slave02 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1339 | Slave02 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1340 | Slave02 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1341 | Slave02 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1342 | Slave02 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1343 | Slave02 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1344 | Slave02 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1345 | Slave02 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1346 | Slave02 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1347 | Slave02 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1348 | Slave02 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1349 | Slave02 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1350 | Slave02 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1351 | Slave02 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1352 | Slave02 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1353 | Slave02 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1354 | Slave02 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1355 | Slave02 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1356 | Slave02 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1357 | Slave02 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1358 | Slave02 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1359 | Slave02 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1360 | Slave02 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1361 | Slave02 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1362 | Slave02 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1363 | Slave02 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1364 | Slave02 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1365 | Slave02 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1366 | Slave02 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1367 | Slave02 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1368 | Slave02 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1369 | Slave02 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1370 | Slave02 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1371 | Slave02 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1372 | Slave02 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1373 | Slave02 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1374 | Slave02 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1375 | Slave02 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1376 | Slave03 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1377 | Slave03 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1378 | Slave03 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1379 | Slave03 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1380 | Slave03 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1381 | Slave03 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1382 | Slave03 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1383 | Slave03 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1384 | Slave03 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1385 | Slave03 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1386 | Slave03 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1387 | Slave03 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1388 | Slave03 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1389 | Slave03 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1390 | Slave03 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1391 | Slave03 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1392 | Slave03 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1393 | Slave03 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1394 | Slave03 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1395 | Slave03 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1396 | Slave03 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1397 | Slave03 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1398 | Slave03 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1399 | Slave03 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1400 | Slave03 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1401 | Slave03 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1402 | Slave03 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1403 | Slave03 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1404 | Slave03 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1405 | Slave03 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1406 | Slave03 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1407 | Slave03 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1408 | Slave03 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1409 | Slave03 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1410 | Slave03 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1411 | Slave03 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1412 | Slave03 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1413 | Slave03 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1414 | Slave03 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1415 | Slave03 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1416 | Slave03 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1417 | Slave03 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1418 | Slave03 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1419 | Slave03 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1420 | Slave03 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1421 | Slave03 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1422 | Slave03 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1423 | Slave03 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1424 | Slave04 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1425 | Slave04 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1426 | Slave04 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1427 | Slave04 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1428 | Slave04 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1429 | Slave04 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1430 | Slave04 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1431 | Slave04 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1432 | Slave04 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1433 | Slave04 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1434 | Slave04 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1435 | Slave04 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1436 | Slave04 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1437 | Slave04 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1438 | Slave04 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1439 | Slave04 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1440 | Slave04 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1441 | Slave04 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1442 | Slave04 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1443 | Slave04 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1444 | Slave04 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1445 | Slave04 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1446 | Slave04 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1447 | Slave04 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1448 | Slave04 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1449 | Slave04 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1450 | Slave04 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1451 | Slave04 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1452 | Slave04 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1453 | Slave04 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1454 | Slave04 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1455 | Slave04 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1456 | Slave04 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1457 | Slave04 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1458 | Slave04 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1459 | Slave04 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1460 | Slave04 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1461 | Slave04 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1462 | Slave04 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1463 | Slave04 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1464 | Slave04 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1465 | Slave04 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1466 | Slave04 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1467 | Slave04 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1468 | Slave04 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1469 | Slave04 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1470 | Slave04 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1471 | Slave04 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1472 | Slave05 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1473 | Slave05 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1474 | Slave05 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1475 | Slave05 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1476 | Slave05 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1477 | Slave05 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1478 | Slave05 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1479 | Slave05 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1480 | Slave05 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1481 | Slave05 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1482 | Slave05 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1483 | Slave05 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1484 | Slave05 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1485 | Slave05 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1486 | Slave05 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1487 | Slave05 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1488 | Slave05 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1489 | Slave05 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1490 | Slave05 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1491 | Slave05 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1492 | Slave05 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1493 | Slave05 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1494 | Slave05 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1495 | Slave05 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1496 | Slave05 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1497 | Slave05 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1498 | Slave05 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1499 | Slave05 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1500 | Slave05 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1501 | Slave05 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1502 | Slave05 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1503 | Slave05 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1504 | Slave05 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1505 | Slave05 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1506 | Slave05 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1507 | Slave05 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1508 | Slave05 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1509 | Slave05 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1510 | Slave05 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1511 | Slave05 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1512 | Slave05 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1513 | Slave05 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1514 | Slave05 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1515 | Slave05 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1516 | Slave05 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1517 | Slave05 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1518 | Slave05 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1519 | Slave05 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1520 | Slave06 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1521 | Slave06 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1522 | Slave06 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1523 | Slave06 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1524 | Slave06 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1525 | Slave06 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1526 | Slave06 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1527 | Slave06 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1528 | Slave06 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1529 | Slave06 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1530 | Slave06 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1531 | Slave06 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1532 | Slave06 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1533 | Slave06 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1534 | Slave06 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1535 | Slave06 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1536 | Slave06 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1537 | Slave06 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1538 | Slave06 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1539 | Slave06 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1540 | Slave06 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1541 | Slave06 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1542 | Slave06 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1543 | Slave06 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1544 | Slave06 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1545 | Slave06 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1546 | Slave06 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1547 | Slave06 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1548 | Slave06 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1549 | Slave06 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1550 | Slave06 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1551 | Slave06 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1552 | Slave06 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1553 | Slave06 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1554 | Slave06 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1555 | Slave06 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1556 | Slave06 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1557 | Slave06 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1558 | Slave06 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1559 | Slave06 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1560 | Slave06 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1561 | Slave06 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1562 | Slave06 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1563 | Slave06 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1564 | Slave06 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1565 | Slave06 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1566 | Slave06 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1567 | Slave06 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1568 | Slave07 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1569 | Slave07 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1570 | Slave07 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1571 | Slave07 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1572 | Slave07 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1573 | Slave07 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1574 | Slave07 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1575 | Slave07 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1576 | Slave07 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1577 | Slave07 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1578 | Slave07 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1579 | Slave07 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1580 | Slave07 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1581 | Slave07 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1582 | Slave07 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1583 | Slave07 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1584 | Slave07 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1585 | Slave07 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1586 | Slave07 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1587 | Slave07 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1588 | Slave07 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1589 | Slave07 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1590 | Slave07 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1591 | Slave07 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1592 | Slave07 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1593 | Slave07 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1594 | Slave07 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1595 | Slave07 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1596 | Slave07 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1597 | Slave07 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1598 | Slave07 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1599 | Slave07 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1600 | Slave07 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1601 | Slave07 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1602 | Slave07 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1603 | Slave07 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1604 | Slave07 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1605 | Slave07 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1606 | Slave07 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1607 | Slave07 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1608 | Slave07 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1609 | Slave07 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1610 | Slave07 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1611 | Slave07 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1612 | Slave07 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1613 | Slave07 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1614 | Slave07 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1615 | Slave07 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1616 | Slave08 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1617 | Slave08 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1618 | Slave08 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1619 | Slave08 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1620 | Slave08 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1621 | Slave08 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1622 | Slave08 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1623 | Slave08 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1624 | Slave08 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1625 | Slave08 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1626 | Slave08 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1627 | Slave08 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1628 | Slave08 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1629 | Slave08 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1630 | Slave08 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1631 | Slave08 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1632 | Slave08 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1633 | Slave08 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1634 | Slave08 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1635 | Slave08 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1636 | Slave08 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1637 | Slave08 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1638 | Slave08 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1639 | Slave08 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1640 | Slave08 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1641 | Slave08 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1642 | Slave08 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1643 | Slave08 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1644 | Slave08 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1645 | Slave08 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1646 | Slave08 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1647 | Slave08 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1648 | Slave08 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1649 | Slave08 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1650 | Slave08 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1651 | Slave08 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1652 | Slave08 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1653 | Slave08 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1654 | Slave08 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1655 | Slave08 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1656 | Slave08 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1657 | Slave08 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1658 | Slave08 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1659 | Slave08 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1660 | Slave08 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1661 | Slave08 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1662 | Slave08 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1663 | Slave08 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1664 | Slave09 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1665 | Slave09 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1666 | Slave09 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1667 | Slave09 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1668 | Slave09 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1669 | Slave09 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1670 | Slave09 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1671 | Slave09 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1672 | Slave09 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1673 | Slave09 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1674 | Slave09 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1675 | Slave09 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1676 | Slave09 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1677 | Slave09 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1678 | Slave09 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1679 | Slave09 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1680 | Slave09 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1681 | Slave09 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1682 | Slave09 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1683 | Slave09 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1684 | Slave09 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1685 | Slave09 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1686 | Slave09 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1687 | Slave09 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1688 | Slave09 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1689 | Slave09 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1690 | Slave09 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1691 | Slave09 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1692 | Slave09 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1693 | Slave09 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1694 | Slave09 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1695 | Slave09 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1696 | Slave09 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1697 | Slave09 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1698 | Slave09 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1699 | Slave09 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1700 | Slave09 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1701 | Slave09 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1702 | Slave09 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1703 | Slave09 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1704 | Slave09 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1705 | Slave09 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1706 | Slave09 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1707 | Slave09 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1708 | Slave09 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1709 | Slave09 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1710 | Slave09 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1711 | Slave09 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1712 | Slave10 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1713 | Slave10 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1714 | Slave10 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1715 | Slave10 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1716 | Slave10 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1717 | Slave10 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1718 | Slave10 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1719 | Slave10 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1720 | Slave10 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1721 | Slave10 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1722 | Slave10 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1723 | Slave10 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1724 | Slave10 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1725 | Slave10 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1726 | Slave10 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1727 | Slave10 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1728 | Slave10 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1729 | Slave10 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1730 | Slave10 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1731 | Slave10 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1732 | Slave10 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1733 | Slave10 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1734 | Slave10 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1735 | Slave10 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1736 | Slave10 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1737 | Slave10 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1738 | Slave10 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1739 | Slave10 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1740 | Slave10 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1741 | Slave10 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1742 | Slave10 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1743 | Slave10 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1744 | Slave10 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1745 | Slave10 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1746 | Slave10 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1747 | Slave10 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1748 | Slave10 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1749 | Slave10 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1750 | Slave10 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1751 | Slave10 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1752 | Slave10 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1753 | Slave10 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1754 | Slave10 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1755 | Slave10 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1756 | Slave10 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1757 | Slave10 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1758 | Slave10 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1759 | Slave10 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1760 | Slave11 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1761 | Slave11 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1762 | Slave11 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1763 | Slave11 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1764 | Slave11 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1765 | Slave11 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1766 | Slave11 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1767 | Slave11 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1768 | Slave11 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1769 | Slave11 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1770 | Slave11 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1771 | Slave11 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1772 | Slave11 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1773 | Slave11 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1774 | Slave11 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1775 | Slave11 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1776 | Slave11 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1777 | Slave11 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1778 | Slave11 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1779 | Slave11 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1780 | Slave11 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1781 | Slave11 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1782 | Slave11 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1783 | Slave11 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1784 | Slave11 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1785 | Slave11 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1786 | Slave11 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1787 | Slave11 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1788 | Slave11 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1789 | Slave11 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1790 | Slave11 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1791 | Slave11 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1792 | Slave11 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1793 | Slave11 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1794 | Slave11 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1795 | Slave11 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1796 | Slave11 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1797 | Slave11 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1798 | Slave11 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1799 | Slave11 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1800 | Slave11 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1801 | Slave11 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1802 | Slave11 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1803 | Slave11 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1804 | Slave11 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1805 | Slave11 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1806 | Slave11 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1807 | Slave11 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1808 | Slave12 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1809 | Slave12 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1810 | Slave12 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1811 | Slave12 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1812 | Slave12 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1813 | Slave12 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1814 | Slave12 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1815 | Slave12 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1816 | Slave12 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1817 | Slave12 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1818 | Slave12 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1819 | Slave12 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1820 | Slave12 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1821 | Slave12 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1822 | Slave12 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1823 | Slave12 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1824 | Slave12 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1825 | Slave12 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1826 | Slave12 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1827 | Slave12 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1828 | Slave12 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1829 | Slave12 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1830 | Slave12 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1831 | Slave12 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1832 | Slave12 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1833 | Slave12 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1834 | Slave12 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1835 | Slave12 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1836 | Slave12 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1837 | Slave12 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1838 | Slave12 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1839 | Slave12 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1840 | Slave12 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1841 | Slave12 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1842 | Slave12 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1843 | Slave12 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1844 | Slave12 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1845 | Slave12 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1846 | Slave12 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1847 | Slave12 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1848 | Slave12 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1849 | Slave12 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1850 | Slave12 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1851 | Slave12 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1852 | Slave12 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1853 | Slave12 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1854 | Slave12 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1855 | Slave12 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1856 | Slave13 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1857 | Slave13 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1858 | Slave13 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1859 | Slave13 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1860 | Slave13 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1861 | Slave13 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1862 | Slave13 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1863 | Slave13 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1864 | Slave13 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1865 | Slave13 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1866 | Slave13 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1867 | Slave13 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1868 | Slave13 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1869 | Slave13 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1870 | Slave13 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1871 | Slave13 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1872 | Slave13 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1873 | Slave13 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1874 | Slave13 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1875 | Slave13 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1876 | Slave13 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1877 | Slave13 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1878 | Slave13 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1879 | Slave13 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1880 | Slave13 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1881 | Slave13 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1882 | Slave13 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1883 | Slave13 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1884 | Slave13 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1885 | Slave13 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1886 | Slave13 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1887 | Slave13 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1888 | Slave13 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1889 | Slave13 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1890 | Slave13 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1891 | Slave13 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1892 | Slave13 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1893 | Slave13 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1894 | Slave13 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1895 | Slave13 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1896 | Slave13 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1897 | Slave13 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1898 | Slave13 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1899 | Slave13 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1900 | Slave13 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1901 | Slave13 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1902 | Slave13 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1903 | Slave13 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1904 | Slave14 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1905 | Slave14 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1906 | Slave14 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1907 | Slave14 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1908 | Slave14 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1909 | Slave14 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1910 | Slave14 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1911 | Slave14 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1912 | Slave14 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1913 | Slave14 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1914 | Slave14 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1915 | Slave14 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1916 | Slave14 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1917 | Slave14 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1918 | Slave14 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1919 | Slave14 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1920 | Slave14 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1921 | Slave14 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1922 | Slave14 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1923 | Slave14 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1924 | Slave14 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1925 | Slave14 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1926 | Slave14 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1927 | Slave14 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1928 | Slave14 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1929 | Slave14 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1930 | Slave14 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1931 | Slave14 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1932 | Slave14 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1933 | Slave14 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1934 | Slave14 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1935 | Slave14 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1936 | Slave14 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1937 | Slave14 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1938 | Slave14 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1939 | Slave14 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1940 | Slave14 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1941 | Slave14 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1942 | Slave14 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1943 | Slave14 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1944 | Slave14 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1945 | Slave14 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1946 | Slave14 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1947 | Slave14 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1948 | Slave14 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1949 | Slave14 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1950 | Slave14 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1951 | Slave14 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1952 | Slave15 Outlet Port01 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1953 | Slave15 Outlet Port02 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1954 | Slave15 Outlet Port03 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1955 | Slave15 Outlet Port04 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1956 | Slave15 Outlet Port05 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1957 | Slave15 Outlet Port06 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1958 | Slave15 Outlet Port07 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1959 | Slave15 Outlet Port08 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1960 | Slave15 Outlet Port09 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1961 | Slave15 Outlet Port10 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1962 | Slave15 Outlet Port11 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1963 | Slave15 Outlet Port12 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1964 | Slave15 Outlet Port13 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1965 | Slave15 Outlet Port14 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1966 | Slave15 Outlet Port15 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1967 | Slave15 Outlet Port16 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1968 | Slave15 Outlet Port17 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1969 | Slave15 Outlet Port18 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1970 | Slave15 Outlet Port19 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1971 | Slave15 Outlet Port20 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1972 | Slave15 Outlet Port21 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1973 | Slave15 Outlet Port22 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1974 | Slave15 Outlet Port23 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1975 | Slave15 Outlet Port24 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1976 | Slave15 Outlet Port25 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1977 | Slave15 Outlet Port26 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1978 | Slave15 Outlet Port27 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1979 | Slave15 Outlet Port28 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1980 | Slave15 Outlet Port29 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1981 | Slave15 Outlet Port30 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1982 | Slave15 Outlet Port31 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1983 | Slave15 Outlet Port32 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1984 | Slave15 Outlet Port33 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1985 | Slave15 Outlet Port34 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1986 | Slave15 Outlet Port35 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1987 | Slave15 Outlet Port36 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1988 | Slave15 Outlet Port37 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1989 | Slave15 Outlet Port38 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1990 | Slave15 Outlet Port39 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1991 | Slave15 Outlet Port40 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1992 | Slave15 Outlet Port41 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1993 | Slave15 Outlet Port42 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1994 | Slave15 Outlet Port43 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1995 | Slave15 Outlet Port44 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1996 | Slave15 Outlet Port45 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1997 | Slave15 Outlet Port46 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1998 | Slave15 Outlet Port47 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
1999 | Slave15 Outlet Port48 Board ID | RO | 2 bytes | Bit0:Force is 1; Bit1:1[0]/3[1] Phase; Bit9:Inlet[0]/Outlet[1];Bit10:Outlet 2P[0]/6P[1];----Bit11: Relay Type. 0 is relay;1 is non-relay;Bit15:A2 Format Bitmap; must is 1
2000 | Master Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2001 | Master Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2002 | Master Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2003 | Master Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2004 | Master Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2005 | Master Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2006 | Master Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2007 | Master Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2008 | Master Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2009 | Master Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2010 | Master Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2011 | Master Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2012 | Master Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2013 | Master Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2014 | Master Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2015 | Master Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2016 | Master Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2017 | Master Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2018 | Master Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2019 | Master Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2020 | Master Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2021 | Master Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2022 | Master Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2023 | Master Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2024 | Master Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2025 | Master Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2026 | Master Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2027 | Master Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2028 | Master Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2029 | Master Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2030 | Master Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2031 | Master Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2032 | Master Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2033 | Master Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2034 | Master Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2035 | Master Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2036 | Master Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2037 | Master Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2038 | Master Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2039 | Master Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2040 | Master Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2041 | Master Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2042 | Master Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2043 | Master Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2044 | Master Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2045 | Master Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2046 | Master Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2047 | Master Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2048 | Slave01 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2049 | Slave01 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2050 | Slave01 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2051 | Slave01 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2052 | Slave01 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2053 | Slave01 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2054 | Slave01 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2055 | Slave01 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2056 | Slave01 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2057 | Slave01 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2058 | Slave01 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2059 | Slave01 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2060 | Slave01 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2061 | Slave01 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2062 | Slave01 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2063 | Slave01 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2064 | Slave01 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2065 | Slave01 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2066 | Slave01 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2067 | Slave01 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2068 | Slave01 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2069 | Slave01 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2070 | Slave01 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2071 | Slave01 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2072 | Slave01 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2073 | Slave01 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2074 | Slave01 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2075 | Slave01 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2076 | Slave01 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2077 | Slave01 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2078 | Slave01 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2079 | Slave01 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2080 | Slave01 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2081 | Slave01 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2082 | Slave01 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2083 | Slave01 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2084 | Slave01 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2085 | Slave01 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2086 | Slave01 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2087 | Slave01 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2088 | Slave01 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2089 | Slave01 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2090 | Slave01 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2091 | Slave01 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2092 | Slave01 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2093 | Slave01 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2094 | Slave01 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2095 | Slave01 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2096 | Slave02 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2097 | Slave02 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2098 | Slave02 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2099 | Slave02 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2100 | Slave02 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2101 | Slave02 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2102 | Slave02 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2103 | Slave02 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2104 | Slave02 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2105 | Slave02 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2106 | Slave02 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2107 | Slave02 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2108 | Slave02 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2109 | Slave02 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2110 | Slave02 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2111 | Slave02 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2112 | Slave02 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2113 | Slave02 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2114 | Slave02 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2115 | Slave02 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2116 | Slave02 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2117 | Slave02 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2118 | Slave02 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2119 | Slave02 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2120 | Slave02 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2121 | Slave02 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2122 | Slave02 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2123 | Slave02 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2124 | Slave02 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2125 | Slave02 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2126 | Slave02 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2127 | Slave02 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2128 | Slave02 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2129 | Slave02 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2130 | Slave02 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2131 | Slave02 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2132 | Slave02 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2133 | Slave02 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2134 | Slave02 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2135 | Slave02 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2136 | Slave02 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2137 | Slave02 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2138 | Slave02 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2139 | Slave02 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2140 | Slave02 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2141 | Slave02 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2142 | Slave02 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2143 | Slave02 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2144 | Slave03 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2145 | Slave03 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2146 | Slave03 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2147 | Slave03 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2148 | Slave03 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2149 | Slave03 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2150 | Slave03 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2151 | Slave03 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2152 | Slave03 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2153 | Slave03 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2154 | Slave03 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2155 | Slave03 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2156 | Slave03 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2157 | Slave03 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2158 | Slave03 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2159 | Slave03 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2160 | Slave03 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2161 | Slave03 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2162 | Slave03 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2163 | Slave03 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2164 | Slave03 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2165 | Slave03 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2166 | Slave03 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2167 | Slave03 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2168 | Slave03 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2169 | Slave03 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2170 | Slave03 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2171 | Slave03 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2172 | Slave03 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2173 | Slave03 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2174 | Slave03 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2175 | Slave03 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2176 | Slave03 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2177 | Slave03 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2178 | Slave03 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2179 | Slave03 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2180 | Slave03 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2181 | Slave03 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2182 | Slave03 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2183 | Slave03 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2184 | Slave03 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2185 | Slave03 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2186 | Slave03 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2187 | Slave03 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2188 | Slave03 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2189 | Slave03 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2190 | Slave03 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2191 | Slave03 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2192 | Slave04 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2193 | Slave04 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2194 | Slave04 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2195 | Slave04 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2196 | Slave04 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2197 | Slave04 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2198 | Slave04 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2199 | Slave04 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2200 | Slave04 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2201 | Slave04 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2202 | Slave04 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2203 | Slave04 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2204 | Slave04 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2205 | Slave04 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2206 | Slave04 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2207 | Slave04 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2208 | Slave04 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2209 | Slave04 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2210 | Slave04 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2211 | Slave04 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2212 | Slave04 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2213 | Slave04 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2214 | Slave04 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2215 | Slave04 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2216 | Slave04 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2217 | Slave04 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2218 | Slave04 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2219 | Slave04 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2220 | Slave04 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2221 | Slave04 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2222 | Slave04 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2223 | Slave04 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2224 | Slave04 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2225 | Slave04 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2226 | Slave04 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2227 | Slave04 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2228 | Slave04 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2229 | Slave04 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2230 | Slave04 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2231 | Slave04 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2232 | Slave04 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2233 | Slave04 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2234 | Slave04 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2235 | Slave04 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2236 | Slave04 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2237 | Slave04 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2238 | Slave04 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2239 | Slave04 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2240 | Slave05 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2241 | Slave05 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2242 | Slave05 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2243 | Slave05 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2244 | Slave05 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2245 | Slave05 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2246 | Slave05 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2247 | Slave05 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2248 | Slave05 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2249 | Slave05 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2250 | Slave05 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2251 | Slave05 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2252 | Slave05 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2253 | Slave05 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2254 | Slave05 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2255 | Slave05 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2256 | Slave05 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2257 | Slave05 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2258 | Slave05 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2259 | Slave05 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2260 | Slave05 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2261 | Slave05 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2262 | Slave05 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2263 | Slave05 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2264 | Slave05 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2265 | Slave05 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2266 | Slave05 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2267 | Slave05 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2268 | Slave05 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2269 | Slave05 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2270 | Slave05 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2271 | Slave05 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2272 | Slave05 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2273 | Slave05 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2274 | Slave05 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2275 | Slave05 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2276 | Slave05 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2277 | Slave05 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2278 | Slave05 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2279 | Slave05 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2280 | Slave05 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2281 | Slave05 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2282 | Slave05 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2283 | Slave05 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2284 | Slave05 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2285 | Slave05 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2286 | Slave05 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2287 | Slave05 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2288 | Slave06 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2289 | Slave06 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2290 | Slave06 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2291 | Slave06 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2292 | Slave06 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2293 | Slave06 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2294 | Slave06 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2295 | Slave06 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2296 | Slave06 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2297 | Slave06 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2298 | Slave06 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2299 | Slave06 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2300 | Slave06 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2301 | Slave06 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2302 | Slave06 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2303 | Slave06 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2304 | Slave06 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2305 | Slave06 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2306 | Slave06 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2307 | Slave06 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2308 | Slave06 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2309 | Slave06 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2310 | Slave06 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2311 | Slave06 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2312 | Slave06 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2313 | Slave06 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2314 | Slave06 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2315 | Slave06 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2316 | Slave06 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2317 | Slave06 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2318 | Slave06 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2319 | Slave06 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2320 | Slave06 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2321 | Slave06 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2322 | Slave06 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2323 | Slave06 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2324 | Slave06 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2325 | Slave06 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2326 | Slave06 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2327 | Slave06 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2328 | Slave06 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2329 | Slave06 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2330 | Slave06 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2331 | Slave06 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2332 | Slave06 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2333 | Slave06 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2334 | Slave06 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2335 | Slave06 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2336 | Slave07 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2337 | Slave07 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2338 | Slave07 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2339 | Slave07 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2340 | Slave07 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2341 | Slave07 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2342 | Slave07 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2343 | Slave07 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2344 | Slave07 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2345 | Slave07 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2346 | Slave07 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2347 | Slave07 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2348 | Slave07 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2349 | Slave07 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2350 | Slave07 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2351 | Slave07 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2352 | Slave07 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2353 | Slave07 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2354 | Slave07 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2355 | Slave07 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2356 | Slave07 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2357 | Slave07 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2358 | Slave07 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2359 | Slave07 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2360 | Slave07 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2361 | Slave07 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2362 | Slave07 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2363 | Slave07 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2364 | Slave07 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2365 | Slave07 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2366 | Slave07 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2367 | Slave07 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2368 | Slave07 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2369 | Slave07 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2370 | Slave07 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2371 | Slave07 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2372 | Slave07 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2373 | Slave07 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2374 | Slave07 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2375 | Slave07 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2376 | Slave07 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2377 | Slave07 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2378 | Slave07 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2379 | Slave07 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2380 | Slave07 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2381 | Slave07 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2382 | Slave07 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2383 | Slave07 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2384 | Slave08 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2385 | Slave08 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2386 | Slave08 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2387 | Slave08 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2388 | Slave08 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2389 | Slave08 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2390 | Slave08 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2391 | Slave08 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2392 | Slave08 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2393 | Slave08 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2394 | Slave08 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2395 | Slave08 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2396 | Slave08 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2397 | Slave08 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2398 | Slave08 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2399 | Slave08 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2400 | Slave08 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2401 | Slave08 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2402 | Slave08 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2403 | Slave08 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2404 | Slave08 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2405 | Slave08 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2406 | Slave08 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2407 | Slave08 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2408 | Slave08 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2409 | Slave08 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2410 | Slave08 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2411 | Slave08 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2412 | Slave08 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2413 | Slave08 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2414 | Slave08 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2415 | Slave08 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2416 | Slave08 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2417 | Slave08 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2418 | Slave08 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2419 | Slave08 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2420 | Slave08 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2421 | Slave08 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2422 | Slave08 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2423 | Slave08 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2424 | Slave08 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2425 | Slave08 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2426 | Slave08 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2427 | Slave08 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2428 | Slave08 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2429 | Slave08 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2430 | Slave08 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2431 | Slave08 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2432 | Slave09 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2433 | Slave09 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2434 | Slave09 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2435 | Slave09 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2436 | Slave09 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2437 | Slave09 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2438 | Slave09 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2439 | Slave09 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2440 | Slave09 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2441 | Slave09 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2442 | Slave09 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2443 | Slave09 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2444 | Slave09 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2445 | Slave09 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2446 | Slave09 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2447 | Slave09 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2448 | Slave09 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2449 | Slave09 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2450 | Slave09 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2451 | Slave09 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2452 | Slave09 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2453 | Slave09 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2454 | Slave09 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2455 | Slave09 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2456 | Slave09 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2457 | Slave09 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2458 | Slave09 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2459 | Slave09 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2460 | Slave09 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2461 | Slave09 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2462 | Slave09 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2463 | Slave09 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2464 | Slave09 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2465 | Slave09 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2466 | Slave09 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2467 | Slave09 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2468 | Slave09 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2469 | Slave09 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2470 | Slave09 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2471 | Slave09 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2472 | Slave09 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2473 | Slave09 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2474 | Slave09 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2475 | Slave09 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2476 | Slave09 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2477 | Slave09 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2478 | Slave09 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2479 | Slave09 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2480 | Slave10 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2481 | Slave10 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2482 | Slave10 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2483 | Slave10 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2484 | Slave10 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2485 | Slave10 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2486 | Slave10 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2487 | Slave10 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2488 | Slave10 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2489 | Slave10 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2490 | Slave10 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2491 | Slave10 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2492 | Slave10 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2493 | Slave10 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2494 | Slave10 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2495 | Slave10 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2496 | Slave10 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2497 | Slave10 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2498 | Slave10 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2499 | Slave10 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2500 | Slave10 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2501 | Slave10 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2502 | Slave10 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2503 | Slave10 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2504 | Slave10 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2505 | Slave10 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2506 | Slave10 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2507 | Slave10 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2508 | Slave10 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2509 | Slave10 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2510 | Slave10 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2511 | Slave10 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2512 | Slave10 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2513 | Slave10 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2514 | Slave10 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2515 | Slave10 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2516 | Slave10 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2517 | Slave10 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2518 | Slave10 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2519 | Slave10 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2520 | Slave10 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2521 | Slave10 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2522 | Slave10 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2523 | Slave10 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2524 | Slave10 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2525 | Slave10 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2526 | Slave10 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2527 | Slave10 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2528 | Slave11 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2529 | Slave11 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2530 | Slave11 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2531 | Slave11 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2532 | Slave11 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2533 | Slave11 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2534 | Slave11 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2535 | Slave11 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2536 | Slave11 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2537 | Slave11 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2538 | Slave11 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2539 | Slave11 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2540 | Slave11 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2541 | Slave11 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2542 | Slave11 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2543 | Slave11 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2544 | Slave11 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2545 | Slave11 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2546 | Slave11 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2547 | Slave11 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2548 | Slave11 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2549 | Slave11 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2550 | Slave11 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2551 | Slave11 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2552 | Slave11 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2553 | Slave11 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2554 | Slave11 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2555 | Slave11 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2556 | Slave11 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2557 | Slave11 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2558 | Slave11 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2559 | Slave11 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2560 | Slave11 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2561 | Slave11 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2562 | Slave11 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2563 | Slave11 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2564 | Slave11 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2565 | Slave11 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2566 | Slave11 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2567 | Slave11 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2568 | Slave11 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2569 | Slave11 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2570 | Slave11 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2571 | Slave11 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2572 | Slave11 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2573 | Slave11 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2574 | Slave11 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2575 | Slave11 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2576 | Slave12 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2577 | Slave12 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2578 | Slave12 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2579 | Slave12 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2580 | Slave12 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2581 | Slave12 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2582 | Slave12 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2583 | Slave12 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2584 | Slave12 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2585 | Slave12 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2586 | Slave12 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2587 | Slave12 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2588 | Slave12 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2589 | Slave12 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2590 | Slave12 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2591 | Slave12 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2592 | Slave12 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2593 | Slave12 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2594 | Slave12 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2595 | Slave12 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2596 | Slave12 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2597 | Slave12 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2598 | Slave12 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2599 | Slave12 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2600 | Slave12 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2601 | Slave12 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2602 | Slave12 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2603 | Slave12 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2604 | Slave12 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2605 | Slave12 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2606 | Slave12 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2607 | Slave12 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2608 | Slave12 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2609 | Slave12 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2610 | Slave12 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2611 | Slave12 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2612 | Slave12 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2613 | Slave12 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2614 | Slave12 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2615 | Slave12 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2616 | Slave12 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2617 | Slave12 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2618 | Slave12 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2619 | Slave12 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2620 | Slave12 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2621 | Slave12 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2622 | Slave12 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2623 | Slave12 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2624 | Slave13 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2625 | Slave13 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2626 | Slave13 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2627 | Slave13 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2628 | Slave13 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2629 | Slave13 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2630 | Slave13 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2631 | Slave13 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2632 | Slave13 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2633 | Slave13 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2634 | Slave13 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2635 | Slave13 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2636 | Slave13 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2637 | Slave13 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2638 | Slave13 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2639 | Slave13 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2640 | Slave13 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2641 | Slave13 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2642 | Slave13 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2643 | Slave13 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2644 | Slave13 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2645 | Slave13 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2646 | Slave13 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2647 | Slave13 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2648 | Slave13 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2649 | Slave13 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2650 | Slave13 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2651 | Slave13 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2652 | Slave13 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2653 | Slave13 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2654 | Slave13 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2655 | Slave13 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2656 | Slave13 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2657 | Slave13 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2658 | Slave13 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2659 | Slave13 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2660 | Slave13 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2661 | Slave13 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2662 | Slave13 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2663 | Slave13 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2664 | Slave13 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2665 | Slave13 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2666 | Slave13 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2667 | Slave13 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2668 | Slave13 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2669 | Slave13 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2670 | Slave13 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2671 | Slave13 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2672 | Slave14 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2673 | Slave14 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2674 | Slave14 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2675 | Slave14 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2676 | Slave14 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2677 | Slave14 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2678 | Slave14 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2679 | Slave14 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2680 | Slave14 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2681 | Slave14 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2682 | Slave14 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2683 | Slave14 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2684 | Slave14 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2685 | Slave14 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2686 | Slave14 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2687 | Slave14 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2688 | Slave14 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2689 | Slave14 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2690 | Slave14 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2691 | Slave14 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2692 | Slave14 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2693 | Slave14 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2694 | Slave14 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2695 | Slave14 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2696 | Slave14 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2697 | Slave14 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2698 | Slave14 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2699 | Slave14 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2700 | Slave14 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2701 | Slave14 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2702 | Slave14 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2703 | Slave14 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2704 | Slave14 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2705 | Slave14 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2706 | Slave14 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2707 | Slave14 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2708 | Slave14 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2709 | Slave14 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2710 | Slave14 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2711 | Slave14 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2712 | Slave14 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2713 | Slave14 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2714 | Slave14 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2715 | Slave14 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2716 | Slave14 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2717 | Slave14 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2718 | Slave14 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2719 | Slave14 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2720 | Slave15 Outlet Port01 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2721 | Slave15 Outlet Port02 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2722 | Slave15 Outlet Port03 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2723 | Slave15 Outlet Port04 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2724 | Slave15 Outlet Port05 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2725 | Slave15 Outlet Port06 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2726 | Slave15 Outlet Port07 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2727 | Slave15 Outlet Port08 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2728 | Slave15 Outlet Port09 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2729 | Slave15 Outlet Port10 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2730 | Slave15 Outlet Port11 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2731 | Slave15 Outlet Port12 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2732 | Slave15 Outlet Port13 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2733 | Slave15 Outlet Port14 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2734 | Slave15 Outlet Port15 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2735 | Slave15 Outlet Port16 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2736 | Slave15 Outlet Port17 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2737 | Slave15 Outlet Port18 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2738 | Slave15 Outlet Port19 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2739 | Slave15 Outlet Port20 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2740 | Slave15 Outlet Port21 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2741 | Slave15 Outlet Port22 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2742 | Slave15 Outlet Port23 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2743 | Slave15 Outlet Port24 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2744 | Slave15 Outlet Port25 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2745 | Slave15 Outlet Port26 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2746 | Slave15 Outlet Port27 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2747 | Slave15 Outlet Port28 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2748 | Slave15 Outlet Port29 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2749 | Slave15 Outlet Port30 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2750 | Slave15 Outlet Port31 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2751 | Slave15 Outlet Port32 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2752 | Slave15 Outlet Port33 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2753 | Slave15 Outlet Port34 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2754 | Slave15 Outlet Port35 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2755 | Slave15 Outlet Port36 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2756 | Slave15 Outlet Port37 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2757 | Slave15 Outlet Port38 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2758 | Slave15 Outlet Port39 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2759 | Slave15 Outlet Port40 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2760 | Slave15 Outlet Port41 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2761 | Slave15 Outlet Port42 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2762 | Slave15 Outlet Port43 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2763 | Slave15 Outlet Port44 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2764 | Slave15 Outlet Port45 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2765 | Slave15 Outlet Port46 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2766 | Slave15 Outlet Port47 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2767 | Slave15 Outlet Port48 Relay State | RO | 2 bytes | 1:Relay ON; 0:Relay OFF
2768 | Master Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2769 | Master Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2770 | Master Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2771 | Master Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2772 | Master Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2773 | Master Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2774 | Master Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2775 | Master Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2776 | Master Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2777 | Master Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2778 | Master Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2779 | Master Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2780 | Master Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2781 | Master Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2782 | Master Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2783 | Master Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2784 | Master Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2785 | Master Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2786 | Master Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2787 | Master Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2788 | Master Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2789 | Master Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2790 | Master Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2791 | Master Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2792 | Master Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2793 | Master Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2794 | Master Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2795 | Master Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2796 | Master Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2797 | Master Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2798 | Master Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2799 | Master Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2800 | Master Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2801 | Master Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2802 | Master Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2803 | Master Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2804 | Master Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2805 | Master Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2806 | Master Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2807 | Master Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2808 | Master Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2809 | Master Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2810 | Master Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2811 | Master Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2812 | Master Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2813 | Master Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2814 | Master Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2815 | Master Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2816 | Slave01 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2817 | Slave01 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2818 | Slave01 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2819 | Slave01 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2820 | Slave01 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2821 | Slave01 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2822 | Slave01 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2823 | Slave01 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2824 | Slave01 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2825 | Slave01 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2826 | Slave01 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2827 | Slave01 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2828 | Slave01 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2829 | Slave01 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2830 | Slave01 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2831 | Slave01 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2832 | Slave01 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2833 | Slave01 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2834 | Slave01 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2835 | Slave01 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2836 | Slave01 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2837 | Slave01 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2838 | Slave01 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2839 | Slave01 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2840 | Slave01 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2841 | Slave01 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2842 | Slave01 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2843 | Slave01 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2844 | Slave01 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2845 | Slave01 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2846 | Slave01 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2847 | Slave01 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2848 | Slave01 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2849 | Slave01 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2850 | Slave01 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2851 | Slave01 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2852 | Slave01 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2853 | Slave01 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2854 | Slave01 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2855 | Slave01 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2856 | Slave01 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2857 | Slave01 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2858 | Slave01 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2859 | Slave01 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2860 | Slave01 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2861 | Slave01 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2862 | Slave01 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2863 | Slave01 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2864 | Slave02 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2865 | Slave02 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2866 | Slave02 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2867 | Slave02 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2868 | Slave02 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2869 | Slave02 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2870 | Slave02 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2871 | Slave02 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2872 | Slave02 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2873 | Slave02 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2874 | Slave02 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2875 | Slave02 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2876 | Slave02 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2877 | Slave02 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2878 | Slave02 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2879 | Slave02 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2880 | Slave02 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2881 | Slave02 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2882 | Slave02 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2883 | Slave02 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2884 | Slave02 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2885 | Slave02 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2886 | Slave02 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2887 | Slave02 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2888 | Slave02 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2889 | Slave02 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2890 | Slave02 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2891 | Slave02 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2892 | Slave02 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2893 | Slave02 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2894 | Slave02 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2895 | Slave02 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2896 | Slave02 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2897 | Slave02 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2898 | Slave02 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2899 | Slave02 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2900 | Slave02 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2901 | Slave02 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2902 | Slave02 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2903 | Slave02 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2904 | Slave02 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2905 | Slave02 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2906 | Slave02 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2907 | Slave02 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2908 | Slave02 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2909 | Slave02 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2910 | Slave02 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2911 | Slave02 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2912 | Slave03 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2913 | Slave03 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2914 | Slave03 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2915 | Slave03 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2916 | Slave03 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2917 | Slave03 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2918 | Slave03 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2919 | Slave03 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2920 | Slave03 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2921 | Slave03 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2922 | Slave03 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2923 | Slave03 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2924 | Slave03 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2925 | Slave03 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2926 | Slave03 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2927 | Slave03 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2928 | Slave03 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2929 | Slave03 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2930 | Slave03 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2931 | Slave03 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2932 | Slave03 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2933 | Slave03 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2934 | Slave03 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2935 | Slave03 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2936 | Slave03 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2937 | Slave03 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2938 | Slave03 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2939 | Slave03 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2940 | Slave03 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2941 | Slave03 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2942 | Slave03 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2943 | Slave03 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2944 | Slave03 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2945 | Slave03 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2946 | Slave03 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2947 | Slave03 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2948 | Slave03 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2949 | Slave03 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2950 | Slave03 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2951 | Slave03 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2952 | Slave03 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2953 | Slave03 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2954 | Slave03 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2955 | Slave03 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2956 | Slave03 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2957 | Slave03 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2958 | Slave03 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2959 | Slave03 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2960 | Slave04 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2961 | Slave04 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2962 | Slave04 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2963 | Slave04 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2964 | Slave04 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2965 | Slave04 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2966 | Slave04 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2967 | Slave04 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2968 | Slave04 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2969 | Slave04 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2970 | Slave04 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2971 | Slave04 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2972 | Slave04 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2973 | Slave04 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2974 | Slave04 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2975 | Slave04 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2976 | Slave04 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2977 | Slave04 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2978 | Slave04 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2979 | Slave04 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2980 | Slave04 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2981 | Slave04 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2982 | Slave04 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2983 | Slave04 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2984 | Slave04 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2985 | Slave04 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2986 | Slave04 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2987 | Slave04 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2988 | Slave04 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2989 | Slave04 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2990 | Slave04 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2991 | Slave04 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2992 | Slave04 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2993 | Slave04 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2994 | Slave04 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2995 | Slave04 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2996 | Slave04 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2997 | Slave04 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2998 | Slave04 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
2999 | Slave04 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3000 | Slave04 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3001 | Slave04 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3002 | Slave04 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3003 | Slave04 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3004 | Slave04 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3005 | Slave04 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3006 | Slave04 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3007 | Slave04 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3008 | Slave05 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3009 | Slave05 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3010 | Slave05 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3011 | Slave05 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3012 | Slave05 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3013 | Slave05 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3014 | Slave05 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3015 | Slave05 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3016 | Slave05 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3017 | Slave05 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3018 | Slave05 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3019 | Slave05 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3020 | Slave05 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3021 | Slave05 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3022 | Slave05 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3023 | Slave05 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3024 | Slave05 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3025 | Slave05 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3026 | Slave05 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3027 | Slave05 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3028 | Slave05 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3029 | Slave05 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3030 | Slave05 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3031 | Slave05 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3032 | Slave05 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3033 | Slave05 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3034 | Slave05 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3035 | Slave05 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3036 | Slave05 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3037 | Slave05 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3038 | Slave05 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3039 | Slave05 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3040 | Slave05 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3041 | Slave05 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3042 | Slave05 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3043 | Slave05 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3044 | Slave05 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3045 | Slave05 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3046 | Slave05 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3047 | Slave05 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3048 | Slave05 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3049 | Slave05 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3050 | Slave05 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3051 | Slave05 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3052 | Slave05 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3053 | Slave05 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3054 | Slave05 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3055 | Slave05 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3056 | Slave06 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3057 | Slave06 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3058 | Slave06 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3059 | Slave06 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3060 | Slave06 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3061 | Slave06 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3062 | Slave06 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3063 | Slave06 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3064 | Slave06 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3065 | Slave06 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3066 | Slave06 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3067 | Slave06 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3068 | Slave06 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3069 | Slave06 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3070 | Slave06 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3071 | Slave06 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3072 | Slave06 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3073 | Slave06 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3074 | Slave06 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3075 | Slave06 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3076 | Slave06 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3077 | Slave06 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3078 | Slave06 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3079 | Slave06 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3080 | Slave06 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3081 | Slave06 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3082 | Slave06 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3083 | Slave06 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3084 | Slave06 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3085 | Slave06 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3086 | Slave06 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3087 | Slave06 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3088 | Slave06 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3089 | Slave06 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3090 | Slave06 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3091 | Slave06 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3092 | Slave06 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3093 | Slave06 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3094 | Slave06 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3095 | Slave06 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3096 | Slave06 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3097 | Slave06 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3098 | Slave06 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3099 | Slave06 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3100 | Slave06 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3101 | Slave06 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3102 | Slave06 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3103 | Slave06 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3104 | Slave07 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3105 | Slave07 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3106 | Slave07 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3107 | Slave07 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3108 | Slave07 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3109 | Slave07 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3110 | Slave07 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3111 | Slave07 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3112 | Slave07 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3113 | Slave07 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3114 | Slave07 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3115 | Slave07 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3116 | Slave07 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3117 | Slave07 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3118 | Slave07 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3119 | Slave07 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3120 | Slave07 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3121 | Slave07 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3122 | Slave07 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3123 | Slave07 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3124 | Slave07 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3125 | Slave07 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3126 | Slave07 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3127 | Slave07 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3128 | Slave07 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3129 | Slave07 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3130 | Slave07 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3131 | Slave07 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3132 | Slave07 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3133 | Slave07 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3134 | Slave07 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3135 | Slave07 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3136 | Slave07 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3137 | Slave07 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3138 | Slave07 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3139 | Slave07 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3140 | Slave07 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3141 | Slave07 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3142 | Slave07 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3143 | Slave07 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3144 | Slave07 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3145 | Slave07 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3146 | Slave07 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3147 | Slave07 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3148 | Slave07 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3149 | Slave07 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3150 | Slave07 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3151 | Slave07 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3152 | Slave08 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3153 | Slave08 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3154 | Slave08 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3155 | Slave08 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3156 | Slave08 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3157 | Slave08 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3158 | Slave08 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3159 | Slave08 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3160 | Slave08 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3161 | Slave08 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3162 | Slave08 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3163 | Slave08 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3164 | Slave08 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3165 | Slave08 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3166 | Slave08 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3167 | Slave08 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3168 | Slave08 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3169 | Slave08 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3170 | Slave08 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3171 | Slave08 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3172 | Slave08 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3173 | Slave08 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3174 | Slave08 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3175 | Slave08 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3176 | Slave08 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3177 | Slave08 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3178 | Slave08 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3179 | Slave08 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3180 | Slave08 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3181 | Slave08 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3182 | Slave08 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3183 | Slave08 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3184 | Slave08 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3185 | Slave08 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3186 | Slave08 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3187 | Slave08 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3188 | Slave08 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3189 | Slave08 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3190 | Slave08 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3191 | Slave08 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3192 | Slave08 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3193 | Slave08 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3194 | Slave08 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3195 | Slave08 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3196 | Slave08 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3197 | Slave08 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3198 | Slave08 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3199 | Slave08 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3200 | Slave09 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3201 | Slave09 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3202 | Slave09 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3203 | Slave09 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3204 | Slave09 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3205 | Slave09 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3206 | Slave09 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3207 | Slave09 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3208 | Slave09 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3209 | Slave09 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3210 | Slave09 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3211 | Slave09 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3212 | Slave09 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3213 | Slave09 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3214 | Slave09 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3215 | Slave09 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3216 | Slave09 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3217 | Slave09 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3218 | Slave09 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3219 | Slave09 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3220 | Slave09 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3221 | Slave09 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3222 | Slave09 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3223 | Slave09 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3224 | Slave09 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3225 | Slave09 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3226 | Slave09 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3227 | Slave09 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3228 | Slave09 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3229 | Slave09 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3230 | Slave09 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3231 | Slave09 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3232 | Slave09 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3233 | Slave09 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3234 | Slave09 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3235 | Slave09 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3236 | Slave09 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3237 | Slave09 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3238 | Slave09 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3239 | Slave09 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3240 | Slave09 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3241 | Slave09 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3242 | Slave09 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3243 | Slave09 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3244 | Slave09 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3245 | Slave09 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3246 | Slave09 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3247 | Slave09 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3248 | Slave10 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3249 | Slave10 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3250 | Slave10 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3251 | Slave10 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3252 | Slave10 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3253 | Slave10 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3254 | Slave10 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3255 | Slave10 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3256 | Slave10 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3257 | Slave10 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3258 | Slave10 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3259 | Slave10 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3260 | Slave10 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3261 | Slave10 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3262 | Slave10 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3263 | Slave10 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3264 | Slave10 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3265 | Slave10 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3266 | Slave10 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3267 | Slave10 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3268 | Slave10 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3269 | Slave10 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3270 | Slave10 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3271 | Slave10 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3272 | Slave10 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3273 | Slave10 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3274 | Slave10 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3275 | Slave10 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3276 | Slave10 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3277 | Slave10 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3278 | Slave10 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3279 | Slave10 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3280 | Slave10 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3281 | Slave10 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3282 | Slave10 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3283 | Slave10 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3284 | Slave10 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3285 | Slave10 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3286 | Slave10 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3287 | Slave10 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3288 | Slave10 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3289 | Slave10 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3290 | Slave10 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3291 | Slave10 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3292 | Slave10 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3293 | Slave10 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3294 | Slave10 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3295 | Slave10 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3296 | Slave11 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3297 | Slave11 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3298 | Slave11 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3299 | Slave11 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3300 | Slave11 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3301 | Slave11 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3302 | Slave11 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3303 | Slave11 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3304 | Slave11 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3305 | Slave11 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3306 | Slave11 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3307 | Slave11 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3308 | Slave11 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3309 | Slave11 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3310 | Slave11 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3311 | Slave11 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3312 | Slave11 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3313 | Slave11 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3314 | Slave11 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3315 | Slave11 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3316 | Slave11 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3317 | Slave11 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3318 | Slave11 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3319 | Slave11 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3320 | Slave11 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3321 | Slave11 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3322 | Slave11 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3323 | Slave11 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3324 | Slave11 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3325 | Slave11 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3326 | Slave11 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3327 | Slave11 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3328 | Slave11 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3329 | Slave11 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3330 | Slave11 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3331 | Slave11 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3332 | Slave11 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3333 | Slave11 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3334 | Slave11 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3335 | Slave11 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3336 | Slave11 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3337 | Slave11 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3338 | Slave11 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3339 | Slave11 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3340 | Slave11 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3341 | Slave11 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3342 | Slave11 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3343 | Slave11 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3344 | Slave12 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3345 | Slave12 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3346 | Slave12 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3347 | Slave12 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3348 | Slave12 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3349 | Slave12 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3350 | Slave12 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3351 | Slave12 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3352 | Slave12 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3353 | Slave12 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3354 | Slave12 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3355 | Slave12 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3356 | Slave12 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3357 | Slave12 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3358 | Slave12 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3359 | Slave12 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3360 | Slave12 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3361 | Slave12 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3362 | Slave12 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3363 | Slave12 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3364 | Slave12 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3365 | Slave12 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3366 | Slave12 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3367 | Slave12 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3368 | Slave12 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3369 | Slave12 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3370 | Slave12 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3371 | Slave12 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3372 | Slave12 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3373 | Slave12 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3374 | Slave12 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3375 | Slave12 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3376 | Slave12 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3377 | Slave12 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3378 | Slave12 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3379 | Slave12 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3380 | Slave12 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3381 | Slave12 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3382 | Slave12 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3383 | Slave12 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3384 | Slave12 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3385 | Slave12 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3386 | Slave12 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3387 | Slave12 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3388 | Slave12 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3389 | Slave12 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3390 | Slave12 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3391 | Slave12 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3392 | Slave13 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3393 | Slave13 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3394 | Slave13 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3395 | Slave13 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3396 | Slave13 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3397 | Slave13 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3398 | Slave13 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3399 | Slave13 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3400 | Slave13 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3401 | Slave13 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3402 | Slave13 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3403 | Slave13 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3404 | Slave13 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3405 | Slave13 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3406 | Slave13 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3407 | Slave13 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3408 | Slave13 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3409 | Slave13 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3410 | Slave13 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3411 | Slave13 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3412 | Slave13 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3413 | Slave13 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3414 | Slave13 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3415 | Slave13 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3416 | Slave13 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3417 | Slave13 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3418 | Slave13 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3419 | Slave13 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3420 | Slave13 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3421 | Slave13 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3422 | Slave13 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3423 | Slave13 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3424 | Slave13 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3425 | Slave13 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3426 | Slave13 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3427 | Slave13 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3428 | Slave13 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3429 | Slave13 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3430 | Slave13 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3431 | Slave13 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3432 | Slave13 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3433 | Slave13 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3434 | Slave13 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3435 | Slave13 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3436 | Slave13 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3437 | Slave13 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3438 | Slave13 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3439 | Slave13 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3440 | Slave14 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3441 | Slave14 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3442 | Slave14 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3443 | Slave14 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3444 | Slave14 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3445 | Slave14 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3446 | Slave14 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3447 | Slave14 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3448 | Slave14 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3449 | Slave14 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3450 | Slave14 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3451 | Slave14 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3452 | Slave14 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3453 | Slave14 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3454 | Slave14 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3455 | Slave14 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3456 | Slave14 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3457 | Slave14 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3458 | Slave14 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3459 | Slave14 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3460 | Slave14 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3461 | Slave14 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3462 | Slave14 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3463 | Slave14 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3464 | Slave14 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3465 | Slave14 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3466 | Slave14 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3467 | Slave14 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3468 | Slave14 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3469 | Slave14 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3470 | Slave14 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3471 | Slave14 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3472 | Slave14 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3473 | Slave14 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3474 | Slave14 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3475 | Slave14 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3476 | Slave14 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3477 | Slave14 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3478 | Slave14 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3479 | Slave14 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3480 | Slave14 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3481 | Slave14 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3482 | Slave14 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3483 | Slave14 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3484 | Slave14 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3485 | Slave14 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3486 | Slave14 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3487 | Slave14 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3488 | Slave15 Outlet Port01 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3489 | Slave15 Outlet Port02 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3490 | Slave15 Outlet Port03 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3491 | Slave15 Outlet Port04 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3492 | Slave15 Outlet Port05 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3493 | Slave15 Outlet Port06 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3494 | Slave15 Outlet Port07 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3495 | Slave15 Outlet Port08 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3496 | Slave15 Outlet Port09 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3497 | Slave15 Outlet Port10 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3498 | Slave15 Outlet Port11 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3499 | Slave15 Outlet Port12 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3500 | Slave15 Outlet Port13 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3501 | Slave15 Outlet Port14 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3502 | Slave15 Outlet Port15 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3503 | Slave15 Outlet Port16 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3504 | Slave15 Outlet Port17 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3505 | Slave15 Outlet Port18 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3506 | Slave15 Outlet Port19 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3507 | Slave15 Outlet Port20 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3508 | Slave15 Outlet Port21 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3509 | Slave15 Outlet Port22 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3510 | Slave15 Outlet Port23 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3511 | Slave15 Outlet Port24 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3512 | Slave15 Outlet Port25 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3513 | Slave15 Outlet Port26 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3514 | Slave15 Outlet Port27 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3515 | Slave15 Outlet Port28 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3516 | Slave15 Outlet Port29 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3517 | Slave15 Outlet Port30 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3518 | Slave15 Outlet Port31 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3519 | Slave15 Outlet Port32 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3520 | Slave15 Outlet Port33 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3521 | Slave15 Outlet Port34 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3522 | Slave15 Outlet Port35 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3523 | Slave15 Outlet Port36 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3524 | Slave15 Outlet Port37 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3525 | Slave15 Outlet Port38 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3526 | Slave15 Outlet Port39 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3527 | Slave15 Outlet Port40 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3528 | Slave15 Outlet Port41 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3529 | Slave15 Outlet Port42 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3530 | Slave15 Outlet Port43 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3531 | Slave15 Outlet Port44 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3532 | Slave15 Outlet Port45 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3533 | Slave15 Outlet Port46 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3534 | Slave15 Outlet Port47 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3535 | Slave15 Outlet Port48 Status | RO | 2 bytes | Bit0:Event Warning; Bit1:Event Critical; Bit2:Over Current Warning; Bit3:Over Current Critical; Bit4:Over Power Warning; Bit5:Over Power Critical
3536 | Master Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3537 | Master Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3538 | Master Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3539 | Master Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3540 | Master Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3541 | Master Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3542 | Master Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3543 | Master Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3544 | Master Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3545 | Master Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3546 | Master Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3547 | Master Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3548 | Master Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3549 | Master Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3550 | Master Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3551 | Master Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3552 | Master Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3553 | Master Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3554 | Master Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3555 | Master Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3556 | Master Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3557 | Master Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3558 | Master Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3559 | Master Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3560 | Master Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3561 | Master Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3562 | Master Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3563 | Master Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3564 | Master Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3565 | Master Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3566 | Master Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3567 | Master Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3568 | Master Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3569 | Master Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3570 | Master Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3571 | Master Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3572 | Master Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3573 | Master Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3574 | Master Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3575 | Master Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3576 | Master Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3577 | Master Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3578 | Master Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3579 | Master Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3580 | Master Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3581 | Master Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3582 | Master Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3583 | Master Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3584 | Slave01 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3585 | Slave01 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3586 | Slave01 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3587 | Slave01 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3588 | Slave01 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3589 | Slave01 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3590 | Slave01 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3591 | Slave01 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3592 | Slave01 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3593 | Slave01 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3594 | Slave01 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3595 | Slave01 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3596 | Slave01 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3597 | Slave01 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3598 | Slave01 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3599 | Slave01 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3600 | Slave01 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3601 | Slave01 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3602 | Slave01 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3603 | Slave01 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3604 | Slave01 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3605 | Slave01 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3606 | Slave01 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3607 | Slave01 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3608 | Slave01 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3609 | Slave01 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3610 | Slave01 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3611 | Slave01 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3612 | Slave01 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3613 | Slave01 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3614 | Slave01 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3615 | Slave01 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3616 | Slave01 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3617 | Slave01 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3618 | Slave01 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3619 | Slave01 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3620 | Slave01 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3621 | Slave01 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3622 | Slave01 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3623 | Slave01 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3624 | Slave01 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3625 | Slave01 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3626 | Slave01 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3627 | Slave01 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3628 | Slave01 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3629 | Slave01 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3630 | Slave01 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3631 | Slave01 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3632 | Slave02 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3633 | Slave02 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3634 | Slave02 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3635 | Slave02 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3636 | Slave02 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3637 | Slave02 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3638 | Slave02 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3639 | Slave02 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3640 | Slave02 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3641 | Slave02 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3642 | Slave02 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3643 | Slave02 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3644 | Slave02 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3645 | Slave02 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3646 | Slave02 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3647 | Slave02 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3648 | Slave02 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3649 | Slave02 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3650 | Slave02 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3651 | Slave02 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3652 | Slave02 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3653 | Slave02 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3654 | Slave02 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3655 | Slave02 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3656 | Slave02 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3657 | Slave02 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3658 | Slave02 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3659 | Slave02 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3660 | Slave02 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3661 | Slave02 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3662 | Slave02 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3663 | Slave02 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3664 | Slave02 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3665 | Slave02 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3666 | Slave02 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3667 | Slave02 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3668 | Slave02 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3669 | Slave02 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3670 | Slave02 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3671 | Slave02 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3672 | Slave02 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3673 | Slave02 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3674 | Slave02 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3675 | Slave02 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3676 | Slave02 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3677 | Slave02 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3678 | Slave02 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3679 | Slave02 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3680 | Slave03 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3681 | Slave03 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3682 | Slave03 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3683 | Slave03 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3684 | Slave03 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3685 | Slave03 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3686 | Slave03 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3687 | Slave03 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3688 | Slave03 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3689 | Slave03 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3690 | Slave03 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3691 | Slave03 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3692 | Slave03 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3693 | Slave03 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3694 | Slave03 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3695 | Slave03 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3696 | Slave03 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3697 | Slave03 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3698 | Slave03 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3699 | Slave03 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3700 | Slave03 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3701 | Slave03 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3702 | Slave03 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3703 | Slave03 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3704 | Slave03 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3705 | Slave03 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3706 | Slave03 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3707 | Slave03 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3708 | Slave03 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3709 | Slave03 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3710 | Slave03 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3711 | Slave03 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3712 | Slave03 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3713 | Slave03 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3714 | Slave03 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3715 | Slave03 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3716 | Slave03 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3717 | Slave03 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3718 | Slave03 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3719 | Slave03 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3720 | Slave03 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3721 | Slave03 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3722 | Slave03 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3723 | Slave03 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3724 | Slave03 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3725 | Slave03 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3726 | Slave03 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3727 | Slave03 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3728 | Slave04 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3729 | Slave04 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3730 | Slave04 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3731 | Slave04 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3732 | Slave04 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3733 | Slave04 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3734 | Slave04 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3735 | Slave04 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3736 | Slave04 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3737 | Slave04 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3738 | Slave04 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3739 | Slave04 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3740 | Slave04 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3741 | Slave04 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3742 | Slave04 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3743 | Slave04 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3744 | Slave04 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3745 | Slave04 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3746 | Slave04 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3747 | Slave04 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3748 | Slave04 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3749 | Slave04 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3750 | Slave04 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3751 | Slave04 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3752 | Slave04 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3753 | Slave04 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3754 | Slave04 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3755 | Slave04 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3756 | Slave04 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3757 | Slave04 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3758 | Slave04 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3759 | Slave04 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3760 | Slave04 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3761 | Slave04 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3762 | Slave04 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3763 | Slave04 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3764 | Slave04 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3765 | Slave04 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3766 | Slave04 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3767 | Slave04 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3768 | Slave04 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3769 | Slave04 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3770 | Slave04 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3771 | Slave04 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3772 | Slave04 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3773 | Slave04 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3774 | Slave04 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3775 | Slave04 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3776 | Slave05 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3777 | Slave05 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3778 | Slave05 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3779 | Slave05 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3780 | Slave05 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3781 | Slave05 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3782 | Slave05 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3783 | Slave05 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3784 | Slave05 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3785 | Slave05 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3786 | Slave05 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3787 | Slave05 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3788 | Slave05 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3789 | Slave05 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3790 | Slave05 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3791 | Slave05 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3792 | Slave05 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3793 | Slave05 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3794 | Slave05 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3795 | Slave05 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3796 | Slave05 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3797 | Slave05 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3798 | Slave05 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3799 | Slave05 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3800 | Slave05 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3801 | Slave05 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3802 | Slave05 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3803 | Slave05 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3804 | Slave05 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3805 | Slave05 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3806 | Slave05 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3807 | Slave05 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3808 | Slave05 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3809 | Slave05 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3810 | Slave05 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3811 | Slave05 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3812 | Slave05 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3813 | Slave05 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3814 | Slave05 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3815 | Slave05 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3816 | Slave05 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3817 | Slave05 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3818 | Slave05 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3819 | Slave05 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3820 | Slave05 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3821 | Slave05 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3822 | Slave05 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3823 | Slave05 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3824 | Slave06 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3825 | Slave06 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3826 | Slave06 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3827 | Slave06 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3828 | Slave06 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3829 | Slave06 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3830 | Slave06 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3831 | Slave06 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3832 | Slave06 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3833 | Slave06 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3834 | Slave06 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3835 | Slave06 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3836 | Slave06 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3837 | Slave06 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3838 | Slave06 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3839 | Slave06 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3840 | Slave06 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3841 | Slave06 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3842 | Slave06 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3843 | Slave06 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3844 | Slave06 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3845 | Slave06 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3846 | Slave06 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3847 | Slave06 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3848 | Slave06 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3849 | Slave06 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3850 | Slave06 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3851 | Slave06 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3852 | Slave06 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3853 | Slave06 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3854 | Slave06 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3855 | Slave06 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3856 | Slave06 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3857 | Slave06 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3858 | Slave06 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3859 | Slave06 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3860 | Slave06 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3861 | Slave06 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3862 | Slave06 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3863 | Slave06 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3864 | Slave06 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3865 | Slave06 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3866 | Slave06 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3867 | Slave06 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3868 | Slave06 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3869 | Slave06 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3870 | Slave06 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3871 | Slave06 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3872 | Slave07 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3873 | Slave07 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3874 | Slave07 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3875 | Slave07 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3876 | Slave07 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3877 | Slave07 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3878 | Slave07 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3879 | Slave07 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3880 | Slave07 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3881 | Slave07 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3882 | Slave07 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3883 | Slave07 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3884 | Slave07 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3885 | Slave07 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3886 | Slave07 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3887 | Slave07 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3888 | Slave07 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3889 | Slave07 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3890 | Slave07 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3891 | Slave07 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3892 | Slave07 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3893 | Slave07 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3894 | Slave07 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3895 | Slave07 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3896 | Slave07 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3897 | Slave07 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3898 | Slave07 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3899 | Slave07 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3900 | Slave07 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3901 | Slave07 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3902 | Slave07 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3903 | Slave07 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3904 | Slave07 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3905 | Slave07 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3906 | Slave07 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3907 | Slave07 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3908 | Slave07 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3909 | Slave07 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3910 | Slave07 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3911 | Slave07 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3912 | Slave07 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3913 | Slave07 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3914 | Slave07 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3915 | Slave07 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3916 | Slave07 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3917 | Slave07 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3918 | Slave07 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3919 | Slave07 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3920 | Slave08 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3921 | Slave08 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3922 | Slave08 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3923 | Slave08 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3924 | Slave08 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3925 | Slave08 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3926 | Slave08 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3927 | Slave08 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3928 | Slave08 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3929 | Slave08 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3930 | Slave08 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3931 | Slave08 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3932 | Slave08 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3933 | Slave08 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3934 | Slave08 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3935 | Slave08 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3936 | Slave08 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3937 | Slave08 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3938 | Slave08 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3939 | Slave08 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3940 | Slave08 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3941 | Slave08 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3942 | Slave08 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3943 | Slave08 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3944 | Slave08 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3945 | Slave08 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3946 | Slave08 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3947 | Slave08 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3948 | Slave08 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3949 | Slave08 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3950 | Slave08 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3951 | Slave08 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
3952 | Slave08 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
3953 | Slave08 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
3954 | Slave08 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
3955 | Slave08 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
3956 | Slave08 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
3957 | Slave08 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
3958 | Slave08 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
3959 | Slave08 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
3960 | Slave08 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
3961 | Slave08 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
3962 | Slave08 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
3963 | Slave08 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
3964 | Slave08 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
3965 | Slave08 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
3966 | Slave08 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
3967 | Slave08 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
3968 | Slave09 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
3969 | Slave09 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
3970 | Slave09 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
3971 | Slave09 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
3972 | Slave09 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
3973 | Slave09 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
3974 | Slave09 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
3975 | Slave09 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
3976 | Slave09 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
3977 | Slave09 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
3978 | Slave09 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
3979 | Slave09 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
3980 | Slave09 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
3981 | Slave09 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
3982 | Slave09 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
3983 | Slave09 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
3984 | Slave09 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
3985 | Slave09 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
3986 | Slave09 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
3987 | Slave09 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
3988 | Slave09 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
3989 | Slave09 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
3990 | Slave09 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
3991 | Slave09 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
3992 | Slave09 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
3993 | Slave09 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
3994 | Slave09 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
3995 | Slave09 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
3996 | Slave09 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
3997 | Slave09 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
3998 | Slave09 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
3999 | Slave09 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4000 | Slave09 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4001 | Slave09 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4002 | Slave09 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4003 | Slave09 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4004 | Slave09 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4005 | Slave09 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4006 | Slave09 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4007 | Slave09 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4008 | Slave09 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4009 | Slave09 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4010 | Slave09 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4011 | Slave09 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4012 | Slave09 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4013 | Slave09 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4014 | Slave09 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4015 | Slave09 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4016 | Slave10 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4017 | Slave10 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4018 | Slave10 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4019 | Slave10 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4020 | Slave10 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4021 | Slave10 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4022 | Slave10 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4023 | Slave10 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4024 | Slave10 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4025 | Slave10 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4026 | Slave10 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4027 | Slave10 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4028 | Slave10 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4029 | Slave10 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4030 | Slave10 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4031 | Slave10 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4032 | Slave10 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4033 | Slave10 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4034 | Slave10 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4035 | Slave10 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4036 | Slave10 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4037 | Slave10 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4038 | Slave10 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4039 | Slave10 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4040 | Slave10 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4041 | Slave10 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4042 | Slave10 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4043 | Slave10 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4044 | Slave10 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4045 | Slave10 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4046 | Slave10 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4047 | Slave10 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4048 | Slave10 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4049 | Slave10 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4050 | Slave10 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4051 | Slave10 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4052 | Slave10 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4053 | Slave10 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4054 | Slave10 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4055 | Slave10 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4056 | Slave10 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4057 | Slave10 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4058 | Slave10 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4059 | Slave10 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4060 | Slave10 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4061 | Slave10 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4062 | Slave10 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4063 | Slave10 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4064 | Slave11 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4065 | Slave11 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4066 | Slave11 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4067 | Slave11 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4068 | Slave11 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4069 | Slave11 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4070 | Slave11 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4071 | Slave11 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4072 | Slave11 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4073 | Slave11 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4074 | Slave11 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4075 | Slave11 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4076 | Slave11 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4077 | Slave11 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4078 | Slave11 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4079 | Slave11 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4080 | Slave11 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4081 | Slave11 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4082 | Slave11 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4083 | Slave11 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4084 | Slave11 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4085 | Slave11 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4086 | Slave11 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4087 | Slave11 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4088 | Slave11 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4089 | Slave11 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4090 | Slave11 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4091 | Slave11 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4092 | Slave11 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4093 | Slave11 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4094 | Slave11 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4095 | Slave11 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4096 | Slave11 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4097 | Slave11 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4098 | Slave11 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4099 | Slave11 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4100 | Slave11 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4101 | Slave11 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4102 | Slave11 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4103 | Slave11 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4104 | Slave11 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4105 | Slave11 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4106 | Slave11 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4107 | Slave11 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4108 | Slave11 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4109 | Slave11 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4110 | Slave11 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4111 | Slave11 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4112 | Slave12 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4113 | Slave12 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4114 | Slave12 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4115 | Slave12 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4116 | Slave12 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4117 | Slave12 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4118 | Slave12 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4119 | Slave12 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4120 | Slave12 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4121 | Slave12 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4122 | Slave12 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4123 | Slave12 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4124 | Slave12 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4125 | Slave12 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4126 | Slave12 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4127 | Slave12 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4128 | Slave12 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4129 | Slave12 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4130 | Slave12 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4131 | Slave12 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4132 | Slave12 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4133 | Slave12 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4134 | Slave12 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4135 | Slave12 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4136 | Slave12 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4137 | Slave12 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4138 | Slave12 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4139 | Slave12 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4140 | Slave12 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4141 | Slave12 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4142 | Slave12 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4143 | Slave12 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4144 | Slave12 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4145 | Slave12 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4146 | Slave12 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4147 | Slave12 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4148 | Slave12 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4149 | Slave12 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4150 | Slave12 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4151 | Slave12 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4152 | Slave12 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4153 | Slave12 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4154 | Slave12 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4155 | Slave12 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4156 | Slave12 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4157 | Slave12 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4158 | Slave12 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4159 | Slave12 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4160 | Slave13 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4161 | Slave13 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4162 | Slave13 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4163 | Slave13 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4164 | Slave13 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4165 | Slave13 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4166 | Slave13 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4167 | Slave13 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4168 | Slave13 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4169 | Slave13 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4170 | Slave13 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4171 | Slave13 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4172 | Slave13 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4173 | Slave13 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4174 | Slave13 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4175 | Slave13 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4176 | Slave13 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4177 | Slave13 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4178 | Slave13 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4179 | Slave13 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4180 | Slave13 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4181 | Slave13 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4182 | Slave13 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4183 | Slave13 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4184 | Slave13 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4185 | Slave13 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4186 | Slave13 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4187 | Slave13 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4188 | Slave13 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4189 | Slave13 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4190 | Slave13 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4191 | Slave13 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4192 | Slave13 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4193 | Slave13 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4194 | Slave13 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4195 | Slave13 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4196 | Slave13 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4197 | Slave13 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4198 | Slave13 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4199 | Slave13 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4200 | Slave13 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4201 | Slave13 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4202 | Slave13 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4203 | Slave13 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4204 | Slave13 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4205 | Slave13 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4206 | Slave13 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4207 | Slave13 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4208 | Slave14 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4209 | Slave14 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4210 | Slave14 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4211 | Slave14 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4212 | Slave14 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4213 | Slave14 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4214 | Slave14 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4215 | Slave14 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4216 | Slave14 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4217 | Slave14 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4218 | Slave14 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4219 | Slave14 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4220 | Slave14 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4221 | Slave14 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4222 | Slave14 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4223 | Slave14 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4224 | Slave14 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4225 | Slave14 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4226 | Slave14 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4227 | Slave14 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4228 | Slave14 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4229 | Slave14 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4230 | Slave14 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4231 | Slave14 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4232 | Slave14 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4233 | Slave14 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4234 | Slave14 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4235 | Slave14 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4236 | Slave14 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4237 | Slave14 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4238 | Slave14 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4239 | Slave14 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4240 | Slave14 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4241 | Slave14 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4242 | Slave14 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4243 | Slave14 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4244 | Slave14 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4245 | Slave14 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4246 | Slave14 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4247 | Slave14 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4248 | Slave14 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4249 | Slave14 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4250 | Slave14 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4251 | Slave14 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4252 | Slave14 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4253 | Slave14 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4254 | Slave14 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4255 | Slave14 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4256 | Slave15 Outlet Port01 Voltage | RO | 2 bytes | Unit:0.1V
4257 | Slave15 Outlet Port02 Voltage | RO | 2 bytes | Unit:0.1V
4258 | Slave15 Outlet Port03 Voltage | RO | 2 bytes | Unit:0.1V
4259 | Slave15 Outlet Port04 Voltage | RO | 2 bytes | Unit:0.1V
4260 | Slave15 Outlet Port05 Voltage | RO | 2 bytes | Unit:0.1V
4261 | Slave15 Outlet Port06 Voltage | RO | 2 bytes | Unit:0.1V
4262 | Slave15 Outlet Port07 Voltage | RO | 2 bytes | Unit:0.1V
4263 | Slave15 Outlet Port08 Voltage | RO | 2 bytes | Unit:0.1V
4264 | Slave15 Outlet Port09 Voltage | RO | 2 bytes | Unit:0.1V
4265 | Slave15 Outlet Port10 Voltage | RO | 2 bytes | Unit:0.1V
4266 | Slave15 Outlet Port11 Voltage | RO | 2 bytes | Unit:0.1V
4267 | Slave15 Outlet Port12 Voltage | RO | 2 bytes | Unit:0.1V
4268 | Slave15 Outlet Port13 Voltage | RO | 2 bytes | Unit:0.1V
4269 | Slave15 Outlet Port14 Voltage | RO | 2 bytes | Unit:0.1V
4270 | Slave15 Outlet Port15 Voltage | RO | 2 bytes | Unit:0.1V
4271 | Slave15 Outlet Port16 Voltage | RO | 2 bytes | Unit:0.1V
4272 | Slave15 Outlet Port17 Voltage | RO | 2 bytes | Unit:0.1V
4273 | Slave15 Outlet Port18 Voltage | RO | 2 bytes | Unit:0.1V
4274 | Slave15 Outlet Port19 Voltage | RO | 2 bytes | Unit:0.1V
4275 | Slave15 Outlet Port20 Voltage | RO | 2 bytes | Unit:0.1V
4276 | Slave15 Outlet Port21 Voltage | RO | 2 bytes | Unit:0.1V
4277 | Slave15 Outlet Port22 Voltage | RO | 2 bytes | Unit:0.1V
4278 | Slave15 Outlet Port23 Voltage | RO | 2 bytes | Unit:0.1V
4279 | Slave15 Outlet Port24 Voltage | RO | 2 bytes | Unit:0.1V
4280 | Slave15 Outlet Port25 Voltage | RO | 2 bytes | Unit:0.1V
4281 | Slave15 Outlet Port26 Voltage | RO | 2 bytes | Unit:0.1V
4282 | Slave15 Outlet Port27 Voltage | RO | 2 bytes | Unit:0.1V
4283 | Slave15 Outlet Port28 Voltage | RO | 2 bytes | Unit:0.1V
4284 | Slave15 Outlet Port29 Voltage | RO | 2 bytes | Unit:0.1V
4285 | Slave15 Outlet Port30 Voltage | RO | 2 bytes | Unit:0.1V
4286 | Slave15 Outlet Port31 Voltage | RO | 2 bytes | Unit:0.1V
4287 | Slave15 Outlet Port32 Voltage | RO | 2 bytes | Unit:0.1V
4288 | Slave15 Outlet Port33 Voltage | RO | 2 bytes | Unit:0.1V
4289 | Slave15 Outlet Port34 Voltage | RO | 2 bytes | Unit:0.1V
4290 | Slave15 Outlet Port35 Voltage | RO | 2 bytes | Unit:0.1V
4291 | Slave15 Outlet Port36 Voltage | RO | 2 bytes | Unit:0.1V
4292 | Slave15 Outlet Port37 Voltage | RO | 2 bytes | Unit:0.1V
4293 | Slave15 Outlet Port38 Voltage | RO | 2 bytes | Unit:0.1V
4294 | Slave15 Outlet Port39 Voltage | RO | 2 bytes | Unit:0.1V
4295 | Slave15 Outlet Port40 Voltage | RO | 2 bytes | Unit:0.1V
4296 | Slave15 Outlet Port41 Voltage | RO | 2 bytes | Unit:0.1V
4297 | Slave15 Outlet Port42 Voltage | RO | 2 bytes | Unit:0.1V
4298 | Slave15 Outlet Port43 Voltage | RO | 2 bytes | Unit:0.1V
4299 | Slave15 Outlet Port44 Voltage | RO | 2 bytes | Unit:0.1V
4300 | Slave15 Outlet Port45 Voltage | RO | 2 bytes | Unit:0.1V
4301 | Slave15 Outlet Port46 Voltage | RO | 2 bytes | Unit:0.1V
4302 | Slave15 Outlet Port47 Voltage | RO | 2 bytes | Unit:0.1V
4303 | Slave15 Outlet Port48 Voltage | RO | 2 bytes | Unit:0.1V
4304 | Master Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4305 | Master Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4306 | Master Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4307 | Master Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4308 | Master Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4309 | Master Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4310 | Master Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4311 | Master Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4312 | Master Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4313 | Master Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4314 | Master Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4315 | Master Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4316 | Master Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4317 | Master Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4318 | Master Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4319 | Master Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4320 | Master Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4321 | Master Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4322 | Master Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4323 | Master Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4324 | Master Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4325 | Master Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4326 | Master Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4327 | Master Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4328 | Master Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4329 | Master Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4330 | Master Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4331 | Master Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4332 | Master Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4333 | Master Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4334 | Master Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4335 | Master Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4336 | Master Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4337 | Master Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4338 | Master Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4339 | Master Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4340 | Master Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4341 | Master Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4342 | Master Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4343 | Master Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4344 | Master Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4345 | Master Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4346 | Master Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4347 | Master Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4348 | Master Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4349 | Master Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4350 | Master Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4351 | Master Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4352 | Slave01 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4353 | Slave01 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4354 | Slave01 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4355 | Slave01 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4356 | Slave01 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4357 | Slave01 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4358 | Slave01 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4359 | Slave01 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4360 | Slave01 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4361 | Slave01 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4362 | Slave01 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4363 | Slave01 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4364 | Slave01 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4365 | Slave01 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4366 | Slave01 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4367 | Slave01 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4368 | Slave01 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4369 | Slave01 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4370 | Slave01 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4371 | Slave01 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4372 | Slave01 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4373 | Slave01 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4374 | Slave01 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4375 | Slave01 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4376 | Slave01 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4377 | Slave01 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4378 | Slave01 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4379 | Slave01 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4380 | Slave01 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4381 | Slave01 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4382 | Slave01 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4383 | Slave01 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4384 | Slave01 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4385 | Slave01 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4386 | Slave01 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4387 | Slave01 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4388 | Slave01 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4389 | Slave01 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4390 | Slave01 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4391 | Slave01 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4392 | Slave01 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4393 | Slave01 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4394 | Slave01 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4395 | Slave01 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4396 | Slave01 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4397 | Slave01 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4398 | Slave01 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4399 | Slave01 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4400 | Slave02 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4401 | Slave02 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4402 | Slave02 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4403 | Slave02 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4404 | Slave02 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4405 | Slave02 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4406 | Slave02 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4407 | Slave02 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4408 | Slave02 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4409 | Slave02 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4410 | Slave02 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4411 | Slave02 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4412 | Slave02 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4413 | Slave02 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4414 | Slave02 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4415 | Slave02 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4416 | Slave02 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4417 | Slave02 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4418 | Slave02 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4419 | Slave02 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4420 | Slave02 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4421 | Slave02 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4422 | Slave02 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4423 | Slave02 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4424 | Slave02 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4425 | Slave02 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4426 | Slave02 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4427 | Slave02 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4428 | Slave02 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4429 | Slave02 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4430 | Slave02 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4431 | Slave02 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4432 | Slave02 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4433 | Slave02 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4434 | Slave02 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4435 | Slave02 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4436 | Slave02 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4437 | Slave02 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4438 | Slave02 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4439 | Slave02 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4440 | Slave02 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4441 | Slave02 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4442 | Slave02 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4443 | Slave02 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4444 | Slave02 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4445 | Slave02 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4446 | Slave02 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4447 | Slave02 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4448 | Slave03 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4449 | Slave03 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4450 | Slave03 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4451 | Slave03 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4452 | Slave03 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4453 | Slave03 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4454 | Slave03 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4455 | Slave03 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4456 | Slave03 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4457 | Slave03 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4458 | Slave03 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4459 | Slave03 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4460 | Slave03 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4461 | Slave03 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4462 | Slave03 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4463 | Slave03 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4464 | Slave03 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4465 | Slave03 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4466 | Slave03 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4467 | Slave03 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4468 | Slave03 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4469 | Slave03 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4470 | Slave03 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4471 | Slave03 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4472 | Slave03 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4473 | Slave03 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4474 | Slave03 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4475 | Slave03 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4476 | Slave03 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4477 | Slave03 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4478 | Slave03 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4479 | Slave03 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4480 | Slave03 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4481 | Slave03 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4482 | Slave03 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4483 | Slave03 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4484 | Slave03 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4485 | Slave03 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4486 | Slave03 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4487 | Slave03 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4488 | Slave03 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4489 | Slave03 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4490 | Slave03 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4491 | Slave03 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4492 | Slave03 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4493 | Slave03 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4494 | Slave03 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4495 | Slave03 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4496 | Slave04 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4497 | Slave04 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4498 | Slave04 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4499 | Slave04 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4500 | Slave04 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4501 | Slave04 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4502 | Slave04 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4503 | Slave04 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4504 | Slave04 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4505 | Slave04 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4506 | Slave04 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4507 | Slave04 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4508 | Slave04 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4509 | Slave04 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4510 | Slave04 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4511 | Slave04 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4512 | Slave04 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4513 | Slave04 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4514 | Slave04 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4515 | Slave04 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4516 | Slave04 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4517 | Slave04 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4518 | Slave04 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4519 | Slave04 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4520 | Slave04 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4521 | Slave04 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4522 | Slave04 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4523 | Slave04 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4524 | Slave04 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4525 | Slave04 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4526 | Slave04 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4527 | Slave04 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4528 | Slave04 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4529 | Slave04 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4530 | Slave04 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4531 | Slave04 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4532 | Slave04 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4533 | Slave04 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4534 | Slave04 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4535 | Slave04 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4536 | Slave04 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4537 | Slave04 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4538 | Slave04 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4539 | Slave04 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4540 | Slave04 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4541 | Slave04 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4542 | Slave04 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4543 | Slave04 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4544 | Slave05 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4545 | Slave05 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4546 | Slave05 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4547 | Slave05 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4548 | Slave05 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4549 | Slave05 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4550 | Slave05 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4551 | Slave05 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4552 | Slave05 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4553 | Slave05 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4554 | Slave05 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4555 | Slave05 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4556 | Slave05 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4557 | Slave05 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4558 | Slave05 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4559 | Slave05 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4560 | Slave05 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4561 | Slave05 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4562 | Slave05 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4563 | Slave05 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4564 | Slave05 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4565 | Slave05 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4566 | Slave05 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4567 | Slave05 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4568 | Slave05 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4569 | Slave05 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4570 | Slave05 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4571 | Slave05 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4572 | Slave05 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4573 | Slave05 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4574 | Slave05 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4575 | Slave05 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4576 | Slave05 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4577 | Slave05 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4578 | Slave05 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4579 | Slave05 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4580 | Slave05 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4581 | Slave05 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4582 | Slave05 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4583 | Slave05 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4584 | Slave05 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4585 | Slave05 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4586 | Slave05 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4587 | Slave05 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4588 | Slave05 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4589 | Slave05 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4590 | Slave05 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4591 | Slave05 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4592 | Slave06 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4593 | Slave06 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4594 | Slave06 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4595 | Slave06 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4596 | Slave06 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4597 | Slave06 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4598 | Slave06 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4599 | Slave06 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4600 | Slave06 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4601 | Slave06 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4602 | Slave06 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4603 | Slave06 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4604 | Slave06 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4605 | Slave06 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4606 | Slave06 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4607 | Slave06 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4608 | Slave06 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4609 | Slave06 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4610 | Slave06 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4611 | Slave06 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4612 | Slave06 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4613 | Slave06 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4614 | Slave06 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4615 | Slave06 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4616 | Slave06 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4617 | Slave06 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4618 | Slave06 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4619 | Slave06 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4620 | Slave06 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4621 | Slave06 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4622 | Slave06 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4623 | Slave06 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4624 | Slave06 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4625 | Slave06 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4626 | Slave06 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4627 | Slave06 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4628 | Slave06 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4629 | Slave06 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4630 | Slave06 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4631 | Slave06 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4632 | Slave06 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4633 | Slave06 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4634 | Slave06 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4635 | Slave06 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4636 | Slave06 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4637 | Slave06 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4638 | Slave06 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4639 | Slave06 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4640 | Slave07 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4641 | Slave07 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4642 | Slave07 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4643 | Slave07 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4644 | Slave07 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4645 | Slave07 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4646 | Slave07 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4647 | Slave07 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4648 | Slave07 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4649 | Slave07 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4650 | Slave07 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4651 | Slave07 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4652 | Slave07 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4653 | Slave07 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4654 | Slave07 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4655 | Slave07 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4656 | Slave07 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4657 | Slave07 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4658 | Slave07 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4659 | Slave07 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4660 | Slave07 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4661 | Slave07 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4662 | Slave07 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4663 | Slave07 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4664 | Slave07 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4665 | Slave07 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4666 | Slave07 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4667 | Slave07 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4668 | Slave07 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4669 | Slave07 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4670 | Slave07 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4671 | Slave07 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4672 | Slave07 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4673 | Slave07 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4674 | Slave07 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4675 | Slave07 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4676 | Slave07 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4677 | Slave07 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4678 | Slave07 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4679 | Slave07 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4680 | Slave07 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4681 | Slave07 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4682 | Slave07 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4683 | Slave07 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4684 | Slave07 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4685 | Slave07 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4686 | Slave07 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4687 | Slave07 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4688 | Slave08 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4689 | Slave08 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4690 | Slave08 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4691 | Slave08 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4692 | Slave08 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4693 | Slave08 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4694 | Slave08 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4695 | Slave08 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4696 | Slave08 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4697 | Slave08 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4698 | Slave08 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4699 | Slave08 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4700 | Slave08 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4701 | Slave08 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4702 | Slave08 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4703 | Slave08 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4704 | Slave08 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4705 | Slave08 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4706 | Slave08 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4707 | Slave08 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4708 | Slave08 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4709 | Slave08 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4710 | Slave08 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4711 | Slave08 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4712 | Slave08 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4713 | Slave08 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4714 | Slave08 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4715 | Slave08 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4716 | Slave08 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4717 | Slave08 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4718 | Slave08 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4719 | Slave08 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4720 | Slave08 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4721 | Slave08 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4722 | Slave08 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4723 | Slave08 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4724 | Slave08 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4725 | Slave08 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4726 | Slave08 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4727 | Slave08 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4728 | Slave08 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4729 | Slave08 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4730 | Slave08 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4731 | Slave08 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4732 | Slave08 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4733 | Slave08 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4734 | Slave08 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4735 | Slave08 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4736 | Slave09 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4737 | Slave09 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4738 | Slave09 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4739 | Slave09 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4740 | Slave09 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4741 | Slave09 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4742 | Slave09 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4743 | Slave09 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4744 | Slave09 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4745 | Slave09 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4746 | Slave09 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4747 | Slave09 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4748 | Slave09 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4749 | Slave09 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4750 | Slave09 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4751 | Slave09 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4752 | Slave09 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4753 | Slave09 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4754 | Slave09 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4755 | Slave09 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4756 | Slave09 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4757 | Slave09 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4758 | Slave09 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4759 | Slave09 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4760 | Slave09 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4761 | Slave09 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4762 | Slave09 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4763 | Slave09 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4764 | Slave09 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4765 | Slave09 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4766 | Slave09 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4767 | Slave09 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4768 | Slave09 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4769 | Slave09 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4770 | Slave09 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4771 | Slave09 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4772 | Slave09 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4773 | Slave09 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4774 | Slave09 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4775 | Slave09 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4776 | Slave09 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4777 | Slave09 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4778 | Slave09 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4779 | Slave09 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4780 | Slave09 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4781 | Slave09 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4782 | Slave09 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4783 | Slave09 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4784 | Slave10 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4785 | Slave10 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4786 | Slave10 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4787 | Slave10 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4788 | Slave10 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4789 | Slave10 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4790 | Slave10 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4791 | Slave10 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4792 | Slave10 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4793 | Slave10 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4794 | Slave10 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4795 | Slave10 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4796 | Slave10 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4797 | Slave10 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4798 | Slave10 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4799 | Slave10 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4800 | Slave10 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4801 | Slave10 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4802 | Slave10 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4803 | Slave10 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4804 | Slave10 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4805 | Slave10 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4806 | Slave10 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4807 | Slave10 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4808 | Slave10 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4809 | Slave10 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4810 | Slave10 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4811 | Slave10 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4812 | Slave10 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4813 | Slave10 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4814 | Slave10 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4815 | Slave10 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4816 | Slave10 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4817 | Slave10 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4818 | Slave10 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4819 | Slave10 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4820 | Slave10 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4821 | Slave10 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4822 | Slave10 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4823 | Slave10 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4824 | Slave10 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4825 | Slave10 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4826 | Slave10 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4827 | Slave10 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4828 | Slave10 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4829 | Slave10 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4830 | Slave10 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4831 | Slave10 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4832 | Slave11 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4833 | Slave11 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4834 | Slave11 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4835 | Slave11 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4836 | Slave11 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4837 | Slave11 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4838 | Slave11 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4839 | Slave11 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4840 | Slave11 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4841 | Slave11 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4842 | Slave11 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4843 | Slave11 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4844 | Slave11 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4845 | Slave11 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4846 | Slave11 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4847 | Slave11 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4848 | Slave11 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4849 | Slave11 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4850 | Slave11 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4851 | Slave11 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4852 | Slave11 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4853 | Slave11 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4854 | Slave11 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4855 | Slave11 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4856 | Slave11 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4857 | Slave11 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4858 | Slave11 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4859 | Slave11 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4860 | Slave11 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4861 | Slave11 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4862 | Slave11 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4863 | Slave11 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4864 | Slave11 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4865 | Slave11 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4866 | Slave11 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4867 | Slave11 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4868 | Slave11 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4869 | Slave11 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4870 | Slave11 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4871 | Slave11 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4872 | Slave11 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4873 | Slave11 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4874 | Slave11 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4875 | Slave11 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4876 | Slave11 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4877 | Slave11 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4878 | Slave11 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4879 | Slave11 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4880 | Slave12 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4881 | Slave12 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4882 | Slave12 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4883 | Slave12 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4884 | Slave12 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4885 | Slave12 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4886 | Slave12 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4887 | Slave12 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4888 | Slave12 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4889 | Slave12 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4890 | Slave12 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4891 | Slave12 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4892 | Slave12 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4893 | Slave12 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4894 | Slave12 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4895 | Slave12 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4896 | Slave12 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4897 | Slave12 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4898 | Slave12 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4899 | Slave12 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4900 | Slave12 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4901 | Slave12 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4902 | Slave12 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4903 | Slave12 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4904 | Slave12 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4905 | Slave12 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4906 | Slave12 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4907 | Slave12 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4908 | Slave12 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4909 | Slave12 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4910 | Slave12 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4911 | Slave12 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4912 | Slave12 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4913 | Slave12 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4914 | Slave12 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4915 | Slave12 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4916 | Slave12 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4917 | Slave12 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4918 | Slave12 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4919 | Slave12 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4920 | Slave12 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4921 | Slave12 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4922 | Slave12 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4923 | Slave12 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4924 | Slave12 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4925 | Slave12 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4926 | Slave12 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4927 | Slave12 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4928 | Slave13 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4929 | Slave13 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4930 | Slave13 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4931 | Slave13 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4932 | Slave13 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4933 | Slave13 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4934 | Slave13 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4935 | Slave13 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4936 | Slave13 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4937 | Slave13 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4938 | Slave13 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4939 | Slave13 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4940 | Slave13 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4941 | Slave13 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4942 | Slave13 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4943 | Slave13 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4944 | Slave13 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4945 | Slave13 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4946 | Slave13 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4947 | Slave13 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4948 | Slave13 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4949 | Slave13 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4950 | Slave13 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4951 | Slave13 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
4952 | Slave13 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
4953 | Slave13 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
4954 | Slave13 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
4955 | Slave13 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
4956 | Slave13 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
4957 | Slave13 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
4958 | Slave13 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
4959 | Slave13 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
4960 | Slave13 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
4961 | Slave13 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
4962 | Slave13 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
4963 | Slave13 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
4964 | Slave13 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
4965 | Slave13 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
4966 | Slave13 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
4967 | Slave13 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
4968 | Slave13 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
4969 | Slave13 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
4970 | Slave13 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
4971 | Slave13 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
4972 | Slave13 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
4973 | Slave13 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
4974 | Slave13 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
4975 | Slave13 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
4976 | Slave14 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
4977 | Slave14 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
4978 | Slave14 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
4979 | Slave14 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
4980 | Slave14 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
4981 | Slave14 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
4982 | Slave14 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
4983 | Slave14 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
4984 | Slave14 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
4985 | Slave14 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
4986 | Slave14 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
4987 | Slave14 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
4988 | Slave14 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
4989 | Slave14 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
4990 | Slave14 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
4991 | Slave14 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
4992 | Slave14 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
4993 | Slave14 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
4994 | Slave14 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
4995 | Slave14 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
4996 | Slave14 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
4997 | Slave14 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
4998 | Slave14 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
4999 | Slave14 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
5000 | Slave14 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
5001 | Slave14 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
5002 | Slave14 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
5003 | Slave14 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
5004 | Slave14 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
5005 | Slave14 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
5006 | Slave14 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
5007 | Slave14 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
5008 | Slave14 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
5009 | Slave14 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
5010 | Slave14 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
5011 | Slave14 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
5012 | Slave14 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
5013 | Slave14 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
5014 | Slave14 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
5015 | Slave14 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
5016 | Slave14 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
5017 | Slave14 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
5018 | Slave14 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
5019 | Slave14 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
5020 | Slave14 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
5021 | Slave14 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
5022 | Slave14 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
5023 | Slave14 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
5024 | Slave15 Outlet Port01 Current | RO | 2 bytes | Unit:0.01A
5025 | Slave15 Outlet Port02 Current | RO | 2 bytes | Unit:0.01A
5026 | Slave15 Outlet Port03 Current | RO | 2 bytes | Unit:0.01A
5027 | Slave15 Outlet Port04 Current | RO | 2 bytes | Unit:0.01A
5028 | Slave15 Outlet Port05 Current | RO | 2 bytes | Unit:0.01A
5029 | Slave15 Outlet Port06 Current | RO | 2 bytes | Unit:0.01A
5030 | Slave15 Outlet Port07 Current | RO | 2 bytes | Unit:0.01A
5031 | Slave15 Outlet Port08 Current | RO | 2 bytes | Unit:0.01A
5032 | Slave15 Outlet Port09 Current | RO | 2 bytes | Unit:0.01A
5033 | Slave15 Outlet Port10 Current | RO | 2 bytes | Unit:0.01A
5034 | Slave15 Outlet Port11 Current | RO | 2 bytes | Unit:0.01A
5035 | Slave15 Outlet Port12 Current | RO | 2 bytes | Unit:0.01A
5036 | Slave15 Outlet Port13 Current | RO | 2 bytes | Unit:0.01A
5037 | Slave15 Outlet Port14 Current | RO | 2 bytes | Unit:0.01A
5038 | Slave15 Outlet Port15 Current | RO | 2 bytes | Unit:0.01A
5039 | Slave15 Outlet Port16 Current | RO | 2 bytes | Unit:0.01A
5040 | Slave15 Outlet Port17 Current | RO | 2 bytes | Unit:0.01A
5041 | Slave15 Outlet Port18 Current | RO | 2 bytes | Unit:0.01A
5042 | Slave15 Outlet Port19 Current | RO | 2 bytes | Unit:0.01A
5043 | Slave15 Outlet Port20 Current | RO | 2 bytes | Unit:0.01A
5044 | Slave15 Outlet Port21 Current | RO | 2 bytes | Unit:0.01A
5045 | Slave15 Outlet Port22 Current | RO | 2 bytes | Unit:0.01A
5046 | Slave15 Outlet Port23 Current | RO | 2 bytes | Unit:0.01A
5047 | Slave15 Outlet Port24 Current | RO | 2 bytes | Unit:0.01A
5048 | Slave15 Outlet Port25 Current | RO | 2 bytes | Unit:0.01A
5049 | Slave15 Outlet Port26 Current | RO | 2 bytes | Unit:0.01A
5050 | Slave15 Outlet Port27 Current | RO | 2 bytes | Unit:0.01A
5051 | Slave15 Outlet Port28 Current | RO | 2 bytes | Unit:0.01A
5052 | Slave15 Outlet Port29 Current | RO | 2 bytes | Unit:0.01A
5053 | Slave15 Outlet Port30 Current | RO | 2 bytes | Unit:0.01A
5054 | Slave15 Outlet Port31 Current | RO | 2 bytes | Unit:0.01A
5055 | Slave15 Outlet Port32 Current | RO | 2 bytes | Unit:0.01A
5056 | Slave15 Outlet Port33 Current | RO | 2 bytes | Unit:0.01A
5057 | Slave15 Outlet Port34 Current | RO | 2 bytes | Unit:0.01A
5058 | Slave15 Outlet Port35 Current | RO | 2 bytes | Unit:0.01A
5059 | Slave15 Outlet Port36 Current | RO | 2 bytes | Unit:0.01A
5060 | Slave15 Outlet Port37 Current | RO | 2 bytes | Unit:0.01A
5061 | Slave15 Outlet Port38 Current | RO | 2 bytes | Unit:0.01A
5062 | Slave15 Outlet Port39 Current | RO | 2 bytes | Unit:0.01A
5063 | Slave15 Outlet Port40 Current | RO | 2 bytes | Unit:0.01A
5064 | Slave15 Outlet Port41 Current | RO | 2 bytes | Unit:0.01A
5065 | Slave15 Outlet Port42 Current | RO | 2 bytes | Unit:0.01A
5066 | Slave15 Outlet Port43 Current | RO | 2 bytes | Unit:0.01A
5067 | Slave15 Outlet Port44 Current | RO | 2 bytes | Unit:0.01A
5068 | Slave15 Outlet Port45 Current | RO | 2 bytes | Unit:0.01A
5069 | Slave15 Outlet Port46 Current | RO | 2 bytes | Unit:0.01A
5070 | Slave15 Outlet Port47 Current | RO | 2 bytes | Unit:0.01A
5071 | Slave15 Outlet Port48 Current | RO | 2 bytes | Unit:0.01A
5072 | Master Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5073 | Master Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5074 | Master Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5075 | Master Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5076 | Master Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5077 | Master Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5078 | Master Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5079 | Master Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5080 | Master Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5081 | Master Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5082 | Master Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5083 | Master Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5084 | Master Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5085 | Master Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5086 | Master Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5087 | Master Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5088 | Master Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5089 | Master Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5090 | Master Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5091 | Master Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5092 | Master Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5093 | Master Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5094 | Master Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5095 | Master Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5096 | Master Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5097 | Master Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5098 | Master Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5099 | Master Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5100 | Master Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5101 | Master Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5102 | Master Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5103 | Master Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5104 | Master Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5105 | Master Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5106 | Master Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5107 | Master Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5108 | Master Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5109 | Master Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5110 | Master Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5111 | Master Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5112 | Master Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5113 | Master Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5114 | Master Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5115 | Master Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5116 | Master Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5117 | Master Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5118 | Master Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5119 | Master Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5120 | Slave01 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5121 | Slave01 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5122 | Slave01 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5123 | Slave01 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5124 | Slave01 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5125 | Slave01 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5126 | Slave01 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5127 | Slave01 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5128 | Slave01 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5129 | Slave01 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5130 | Slave01 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5131 | Slave01 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5132 | Slave01 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5133 | Slave01 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5134 | Slave01 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5135 | Slave01 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5136 | Slave01 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5137 | Slave01 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5138 | Slave01 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5139 | Slave01 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5140 | Slave01 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5141 | Slave01 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5142 | Slave01 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5143 | Slave01 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5144 | Slave01 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5145 | Slave01 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5146 | Slave01 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5147 | Slave01 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5148 | Slave01 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5149 | Slave01 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5150 | Slave01 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5151 | Slave01 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5152 | Slave01 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5153 | Slave01 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5154 | Slave01 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5155 | Slave01 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5156 | Slave01 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5157 | Slave01 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5158 | Slave01 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5159 | Slave01 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5160 | Slave01 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5161 | Slave01 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5162 | Slave01 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5163 | Slave01 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5164 | Slave01 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5165 | Slave01 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5166 | Slave01 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5167 | Slave01 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5168 | Slave02 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5169 | Slave02 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5170 | Slave02 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5171 | Slave02 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5172 | Slave02 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5173 | Slave02 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5174 | Slave02 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5175 | Slave02 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5176 | Slave02 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5177 | Slave02 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5178 | Slave02 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5179 | Slave02 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5180 | Slave02 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5181 | Slave02 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5182 | Slave02 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5183 | Slave02 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5184 | Slave02 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5185 | Slave02 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5186 | Slave02 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5187 | Slave02 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5188 | Slave02 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5189 | Slave02 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5190 | Slave02 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5191 | Slave02 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5192 | Slave02 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5193 | Slave02 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5194 | Slave02 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5195 | Slave02 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5196 | Slave02 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5197 | Slave02 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5198 | Slave02 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5199 | Slave02 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5200 | Slave02 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5201 | Slave02 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5202 | Slave02 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5203 | Slave02 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5204 | Slave02 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5205 | Slave02 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5206 | Slave02 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5207 | Slave02 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5208 | Slave02 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5209 | Slave02 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5210 | Slave02 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5211 | Slave02 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5212 | Slave02 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5213 | Slave02 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5214 | Slave02 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5215 | Slave02 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5216 | Slave03 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5217 | Slave03 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5218 | Slave03 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5219 | Slave03 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5220 | Slave03 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5221 | Slave03 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5222 | Slave03 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5223 | Slave03 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5224 | Slave03 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5225 | Slave03 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5226 | Slave03 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5227 | Slave03 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5228 | Slave03 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5229 | Slave03 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5230 | Slave03 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5231 | Slave03 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5232 | Slave03 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5233 | Slave03 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5234 | Slave03 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5235 | Slave03 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5236 | Slave03 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5237 | Slave03 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5238 | Slave03 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5239 | Slave03 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5240 | Slave03 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5241 | Slave03 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5242 | Slave03 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5243 | Slave03 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5244 | Slave03 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5245 | Slave03 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5246 | Slave03 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5247 | Slave03 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5248 | Slave03 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5249 | Slave03 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5250 | Slave03 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5251 | Slave03 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5252 | Slave03 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5253 | Slave03 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5254 | Slave03 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5255 | Slave03 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5256 | Slave03 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5257 | Slave03 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5258 | Slave03 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5259 | Slave03 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5260 | Slave03 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5261 | Slave03 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5262 | Slave03 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5263 | Slave03 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5264 | Slave04 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5265 | Slave04 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5266 | Slave04 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5267 | Slave04 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5268 | Slave04 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5269 | Slave04 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5270 | Slave04 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5271 | Slave04 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5272 | Slave04 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5273 | Slave04 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5274 | Slave04 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5275 | Slave04 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5276 | Slave04 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5277 | Slave04 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5278 | Slave04 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5279 | Slave04 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5280 | Slave04 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5281 | Slave04 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5282 | Slave04 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5283 | Slave04 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5284 | Slave04 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5285 | Slave04 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5286 | Slave04 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5287 | Slave04 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5288 | Slave04 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5289 | Slave04 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5290 | Slave04 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5291 | Slave04 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5292 | Slave04 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5293 | Slave04 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5294 | Slave04 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5295 | Slave04 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5296 | Slave04 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5297 | Slave04 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5298 | Slave04 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5299 | Slave04 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5300 | Slave04 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5301 | Slave04 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5302 | Slave04 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5303 | Slave04 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5304 | Slave04 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5305 | Slave04 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5306 | Slave04 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5307 | Slave04 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5308 | Slave04 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5309 | Slave04 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5310 | Slave04 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5311 | Slave04 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5312 | Slave05 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5313 | Slave05 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5314 | Slave05 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5315 | Slave05 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5316 | Slave05 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5317 | Slave05 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5318 | Slave05 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5319 | Slave05 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5320 | Slave05 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5321 | Slave05 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5322 | Slave05 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5323 | Slave05 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5324 | Slave05 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5325 | Slave05 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5326 | Slave05 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5327 | Slave05 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5328 | Slave05 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5329 | Slave05 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5330 | Slave05 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5331 | Slave05 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5332 | Slave05 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5333 | Slave05 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5334 | Slave05 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5335 | Slave05 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5336 | Slave05 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5337 | Slave05 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5338 | Slave05 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5339 | Slave05 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5340 | Slave05 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5341 | Slave05 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5342 | Slave05 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5343 | Slave05 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5344 | Slave05 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5345 | Slave05 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5346 | Slave05 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5347 | Slave05 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5348 | Slave05 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5349 | Slave05 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5350 | Slave05 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5351 | Slave05 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5352 | Slave05 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5353 | Slave05 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5354 | Slave05 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5355 | Slave05 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5356 | Slave05 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5357 | Slave05 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5358 | Slave05 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5359 | Slave05 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5360 | Slave06 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5361 | Slave06 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5362 | Slave06 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5363 | Slave06 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5364 | Slave06 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5365 | Slave06 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5366 | Slave06 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5367 | Slave06 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5368 | Slave06 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5369 | Slave06 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5370 | Slave06 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5371 | Slave06 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5372 | Slave06 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5373 | Slave06 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5374 | Slave06 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5375 | Slave06 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5376 | Slave06 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5377 | Slave06 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5378 | Slave06 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5379 | Slave06 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5380 | Slave06 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5381 | Slave06 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5382 | Slave06 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5383 | Slave06 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5384 | Slave06 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5385 | Slave06 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5386 | Slave06 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5387 | Slave06 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5388 | Slave06 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5389 | Slave06 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5390 | Slave06 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5391 | Slave06 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5392 | Slave06 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5393 | Slave06 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5394 | Slave06 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5395 | Slave06 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5396 | Slave06 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5397 | Slave06 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5398 | Slave06 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5399 | Slave06 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5400 | Slave06 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5401 | Slave06 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5402 | Slave06 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5403 | Slave06 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5404 | Slave06 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5405 | Slave06 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5406 | Slave06 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5407 | Slave06 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5408 | Slave07 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5409 | Slave07 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5410 | Slave07 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5411 | Slave07 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5412 | Slave07 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5413 | Slave07 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5414 | Slave07 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5415 | Slave07 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5416 | Slave07 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5417 | Slave07 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5418 | Slave07 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5419 | Slave07 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5420 | Slave07 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5421 | Slave07 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5422 | Slave07 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5423 | Slave07 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5424 | Slave07 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5425 | Slave07 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5426 | Slave07 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5427 | Slave07 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5428 | Slave07 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5429 | Slave07 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5430 | Slave07 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5431 | Slave07 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5432 | Slave07 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5433 | Slave07 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5434 | Slave07 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5435 | Slave07 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5436 | Slave07 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5437 | Slave07 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5438 | Slave07 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5439 | Slave07 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5440 | Slave07 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5441 | Slave07 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5442 | Slave07 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5443 | Slave07 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5444 | Slave07 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5445 | Slave07 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5446 | Slave07 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5447 | Slave07 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5448 | Slave07 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5449 | Slave07 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5450 | Slave07 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5451 | Slave07 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5452 | Slave07 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5453 | Slave07 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5454 | Slave07 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5455 | Slave07 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5456 | Slave08 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5457 | Slave08 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5458 | Slave08 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5459 | Slave08 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5460 | Slave08 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5461 | Slave08 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5462 | Slave08 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5463 | Slave08 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5464 | Slave08 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5465 | Slave08 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5466 | Slave08 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5467 | Slave08 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5468 | Slave08 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5469 | Slave08 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5470 | Slave08 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5471 | Slave08 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5472 | Slave08 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5473 | Slave08 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5474 | Slave08 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5475 | Slave08 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5476 | Slave08 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5477 | Slave08 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5478 | Slave08 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5479 | Slave08 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5480 | Slave08 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5481 | Slave08 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5482 | Slave08 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5483 | Slave08 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5484 | Slave08 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5485 | Slave08 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5486 | Slave08 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5487 | Slave08 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5488 | Slave08 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5489 | Slave08 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5490 | Slave08 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5491 | Slave08 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5492 | Slave08 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5493 | Slave08 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5494 | Slave08 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5495 | Slave08 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5496 | Slave08 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5497 | Slave08 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5498 | Slave08 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5499 | Slave08 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5500 | Slave08 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5501 | Slave08 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5502 | Slave08 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5503 | Slave08 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5504 | Slave09 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5505 | Slave09 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5506 | Slave09 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5507 | Slave09 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5508 | Slave09 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5509 | Slave09 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5510 | Slave09 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5511 | Slave09 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5512 | Slave09 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5513 | Slave09 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5514 | Slave09 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5515 | Slave09 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5516 | Slave09 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5517 | Slave09 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5518 | Slave09 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5519 | Slave09 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5520 | Slave09 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5521 | Slave09 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5522 | Slave09 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5523 | Slave09 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5524 | Slave09 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5525 | Slave09 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5526 | Slave09 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5527 | Slave09 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5528 | Slave09 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5529 | Slave09 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5530 | Slave09 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5531 | Slave09 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5532 | Slave09 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5533 | Slave09 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5534 | Slave09 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5535 | Slave09 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5536 | Slave09 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5537 | Slave09 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5538 | Slave09 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5539 | Slave09 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5540 | Slave09 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5541 | Slave09 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5542 | Slave09 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5543 | Slave09 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5544 | Slave09 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5545 | Slave09 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5546 | Slave09 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5547 | Slave09 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5548 | Slave09 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5549 | Slave09 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5550 | Slave09 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5551 | Slave09 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5552 | Slave10 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5553 | Slave10 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5554 | Slave10 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5555 | Slave10 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5556 | Slave10 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5557 | Slave10 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5558 | Slave10 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5559 | Slave10 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5560 | Slave10 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5561 | Slave10 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5562 | Slave10 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5563 | Slave10 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5564 | Slave10 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5565 | Slave10 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5566 | Slave10 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5567 | Slave10 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5568 | Slave10 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5569 | Slave10 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5570 | Slave10 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5571 | Slave10 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5572 | Slave10 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5573 | Slave10 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5574 | Slave10 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5575 | Slave10 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5576 | Slave10 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5577 | Slave10 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5578 | Slave10 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5579 | Slave10 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5580 | Slave10 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5581 | Slave10 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5582 | Slave10 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5583 | Slave10 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5584 | Slave10 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5585 | Slave10 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5586 | Slave10 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5587 | Slave10 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5588 | Slave10 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5589 | Slave10 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5590 | Slave10 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5591 | Slave10 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5592 | Slave10 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5593 | Slave10 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5594 | Slave10 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5595 | Slave10 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5596 | Slave10 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5597 | Slave10 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5598 | Slave10 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5599 | Slave10 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5600 | Slave11 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5601 | Slave11 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5602 | Slave11 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5603 | Slave11 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5604 | Slave11 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5605 | Slave11 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5606 | Slave11 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5607 | Slave11 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5608 | Slave11 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5609 | Slave11 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5610 | Slave11 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5611 | Slave11 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5612 | Slave11 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5613 | Slave11 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5614 | Slave11 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5615 | Slave11 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5616 | Slave11 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5617 | Slave11 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5618 | Slave11 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5619 | Slave11 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5620 | Slave11 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5621 | Slave11 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5622 | Slave11 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5623 | Slave11 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5624 | Slave11 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5625 | Slave11 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5626 | Slave11 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5627 | Slave11 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5628 | Slave11 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5629 | Slave11 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5630 | Slave11 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5631 | Slave11 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5632 | Slave11 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5633 | Slave11 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5634 | Slave11 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5635 | Slave11 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5636 | Slave11 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5637 | Slave11 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5638 | Slave11 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5639 | Slave11 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5640 | Slave11 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5641 | Slave11 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5642 | Slave11 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5643 | Slave11 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5644 | Slave11 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5645 | Slave11 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5646 | Slave11 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5647 | Slave11 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5648 | Slave12 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5649 | Slave12 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5650 | Slave12 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5651 | Slave12 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5652 | Slave12 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5653 | Slave12 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5654 | Slave12 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5655 | Slave12 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5656 | Slave12 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5657 | Slave12 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5658 | Slave12 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5659 | Slave12 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5660 | Slave12 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5661 | Slave12 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5662 | Slave12 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5663 | Slave12 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5664 | Slave12 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5665 | Slave12 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5666 | Slave12 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5667 | Slave12 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5668 | Slave12 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5669 | Slave12 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5670 | Slave12 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5671 | Slave12 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5672 | Slave12 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5673 | Slave12 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5674 | Slave12 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5675 | Slave12 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5676 | Slave12 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5677 | Slave12 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5678 | Slave12 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5679 | Slave12 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5680 | Slave12 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5681 | Slave12 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5682 | Slave12 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5683 | Slave12 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5684 | Slave12 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5685 | Slave12 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5686 | Slave12 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5687 | Slave12 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5688 | Slave12 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5689 | Slave12 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5690 | Slave12 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5691 | Slave12 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5692 | Slave12 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5693 | Slave12 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5694 | Slave12 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5695 | Slave12 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5696 | Slave13 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5697 | Slave13 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5698 | Slave13 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5699 | Slave13 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5700 | Slave13 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5701 | Slave13 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5702 | Slave13 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5703 | Slave13 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5704 | Slave13 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5705 | Slave13 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5706 | Slave13 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5707 | Slave13 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5708 | Slave13 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5709 | Slave13 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5710 | Slave13 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5711 | Slave13 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5712 | Slave13 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5713 | Slave13 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5714 | Slave13 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5715 | Slave13 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5716 | Slave13 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5717 | Slave13 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5718 | Slave13 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5719 | Slave13 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5720 | Slave13 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5721 | Slave13 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5722 | Slave13 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5723 | Slave13 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5724 | Slave13 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5725 | Slave13 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5726 | Slave13 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5727 | Slave13 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5728 | Slave13 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5729 | Slave13 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5730 | Slave13 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5731 | Slave13 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5732 | Slave13 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5733 | Slave13 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5734 | Slave13 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5735 | Slave13 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5736 | Slave13 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5737 | Slave13 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5738 | Slave13 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5739 | Slave13 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5740 | Slave13 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5741 | Slave13 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5742 | Slave13 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5743 | Slave13 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5744 | Slave14 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5745 | Slave14 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5746 | Slave14 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5747 | Slave14 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5748 | Slave14 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5749 | Slave14 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5750 | Slave14 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5751 | Slave14 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5752 | Slave14 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5753 | Slave14 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5754 | Slave14 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5755 | Slave14 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5756 | Slave14 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5757 | Slave14 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5758 | Slave14 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5759 | Slave14 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5760 | Slave14 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5761 | Slave14 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5762 | Slave14 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5763 | Slave14 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5764 | Slave14 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5765 | Slave14 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5766 | Slave14 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5767 | Slave14 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5768 | Slave14 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5769 | Slave14 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5770 | Slave14 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5771 | Slave14 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5772 | Slave14 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5773 | Slave14 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5774 | Slave14 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5775 | Slave14 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5776 | Slave14 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5777 | Slave14 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5778 | Slave14 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5779 | Slave14 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5780 | Slave14 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5781 | Slave14 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5782 | Slave14 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5783 | Slave14 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5784 | Slave14 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5785 | Slave14 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5786 | Slave14 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5787 | Slave14 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5788 | Slave14 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5789 | Slave14 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5790 | Slave14 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5791 | Slave14 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5792 | Slave15 Outlet Port01 PF | RO | 2 bytes | Unit:0.01
5793 | Slave15 Outlet Port02 PF | RO | 2 bytes | Unit:0.01
5794 | Slave15 Outlet Port03 PF | RO | 2 bytes | Unit:0.01
5795 | Slave15 Outlet Port04 PF | RO | 2 bytes | Unit:0.01
5796 | Slave15 Outlet Port05 PF | RO | 2 bytes | Unit:0.01
5797 | Slave15 Outlet Port06 PF | RO | 2 bytes | Unit:0.01
5798 | Slave15 Outlet Port07 PF | RO | 2 bytes | Unit:0.01
5799 | Slave15 Outlet Port08 PF | RO | 2 bytes | Unit:0.01
5800 | Slave15 Outlet Port09 PF | RO | 2 bytes | Unit:0.01
5801 | Slave15 Outlet Port10 PF | RO | 2 bytes | Unit:0.01
5802 | Slave15 Outlet Port11 PF | RO | 2 bytes | Unit:0.01
5803 | Slave15 Outlet Port12 PF | RO | 2 bytes | Unit:0.01
5804 | Slave15 Outlet Port13 PF | RO | 2 bytes | Unit:0.01
5805 | Slave15 Outlet Port14 PF | RO | 2 bytes | Unit:0.01
5806 | Slave15 Outlet Port15 PF | RO | 2 bytes | Unit:0.01
5807 | Slave15 Outlet Port16 PF | RO | 2 bytes | Unit:0.01
5808 | Slave15 Outlet Port17 PF | RO | 2 bytes | Unit:0.01
5809 | Slave15 Outlet Port18 PF | RO | 2 bytes | Unit:0.01
5810 | Slave15 Outlet Port19 PF | RO | 2 bytes | Unit:0.01
5811 | Slave15 Outlet Port20 PF | RO | 2 bytes | Unit:0.01
5812 | Slave15 Outlet Port21 PF | RO | 2 bytes | Unit:0.01
5813 | Slave15 Outlet Port22 PF | RO | 2 bytes | Unit:0.01
5814 | Slave15 Outlet Port23 PF | RO | 2 bytes | Unit:0.01
5815 | Slave15 Outlet Port24 PF | RO | 2 bytes | Unit:0.01
5816 | Slave15 Outlet Port25 PF | RO | 2 bytes | Unit:0.01
5817 | Slave15 Outlet Port26 PF | RO | 2 bytes | Unit:0.01
5818 | Slave15 Outlet Port27 PF | RO | 2 bytes | Unit:0.01
5819 | Slave15 Outlet Port28 PF | RO | 2 bytes | Unit:0.01
5820 | Slave15 Outlet Port29 PF | RO | 2 bytes | Unit:0.01
5821 | Slave15 Outlet Port30 PF | RO | 2 bytes | Unit:0.01
5822 | Slave15 Outlet Port31 PF | RO | 2 bytes | Unit:0.01
5823 | Slave15 Outlet Port32 PF | RO | 2 bytes | Unit:0.01
5824 | Slave15 Outlet Port33 PF | RO | 2 bytes | Unit:0.01
5825 | Slave15 Outlet Port34 PF | RO | 2 bytes | Unit:0.01
5826 | Slave15 Outlet Port35 PF | RO | 2 bytes | Unit:0.01
5827 | Slave15 Outlet Port36 PF | RO | 2 bytes | Unit:0.01
5828 | Slave15 Outlet Port37 PF | RO | 2 bytes | Unit:0.01
5829 | Slave15 Outlet Port38 PF | RO | 2 bytes | Unit:0.01
5830 | Slave15 Outlet Port39 PF | RO | 2 bytes | Unit:0.01
5831 | Slave15 Outlet Port40 PF | RO | 2 bytes | Unit:0.01
5832 | Slave15 Outlet Port41 PF | RO | 2 bytes | Unit:0.01
5833 | Slave15 Outlet Port42 PF | RO | 2 bytes | Unit:0.01
5834 | Slave15 Outlet Port43 PF | RO | 2 bytes | Unit:0.01
5835 | Slave15 Outlet Port44 PF | RO | 2 bytes | Unit:0.01
5836 | Slave15 Outlet Port45 PF | RO | 2 bytes | Unit:0.01
5837 | Slave15 Outlet Port46 PF | RO | 2 bytes | Unit:0.01
5838 | Slave15 Outlet Port47 PF | RO | 2 bytes | Unit:0.01
5839 | Slave15 Outlet Port48 PF | RO | 2 bytes | Unit:0.01
5840 | Master EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5841 | Master EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5842 | Master EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5843 | Master EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5844 | Master EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5845 | Master EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5846 | Master EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5847 | Master EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5848 | Slave01 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5849 | Slave01 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5850 | Slave01 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5851 | Slave01 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5852 | Slave01 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5853 | Slave01 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5854 | Slave01 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5855 | Slave01 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5856 | Slave02 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5857 | Slave02 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5858 | Slave02 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5859 | Slave02 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5860 | Slave02 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5861 | Slave02 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5862 | Slave02 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5863 | Slave02 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5864 | Slave03 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5865 | Slave03 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5866 | Slave03 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5867 | Slave03 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5868 | Slave03 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5869 | Slave03 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5870 | Slave03 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5871 | Slave03 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5872 | Slave04 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5873 | Slave04 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5874 | Slave04 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5875 | Slave04 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5876 | Slave04 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5877 | Slave04 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5878 | Slave04 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5879 | Slave04 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5880 | Slave05 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5881 | Slave05 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5882 | Slave05 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5883 | Slave05 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5884 | Slave05 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5885 | Slave05 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5886 | Slave05 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5887 | Slave05 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5888 | Slave06 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5889 | Slave06 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5890 | Slave06 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5891 | Slave06 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5892 | Slave06 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5893 | Slave06 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5894 | Slave06 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5895 | Slave06 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5896 | Slave07 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5897 | Slave07 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5898 | Slave07 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5899 | Slave07 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5900 | Slave07 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5901 | Slave07 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5902 | Slave07 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5903 | Slave07 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5904 | Slave08 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5905 | Slave08 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5906 | Slave08 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5907 | Slave08 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5908 | Slave08 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5909 | Slave08 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5910 | Slave08 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5911 | Slave08 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5912 | Slave09 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5913 | Slave09 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5914 | Slave09 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5915 | Slave09 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5916 | Slave09 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5917 | Slave09 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5918 | Slave09 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5919 | Slave09 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5920 | Slave10 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5921 | Slave10 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5922 | Slave10 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5923 | Slave10 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5924 | Slave10 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5925 | Slave10 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5926 | Slave10 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5927 | Slave10 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5928 | Slave11 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5929 | Slave11 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5930 | Slave11 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5931 | Slave11 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5932 | Slave11 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5933 | Slave11 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5934 | Slave11 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5935 | Slave11 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5936 | Slave12 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5937 | Slave12 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5938 | Slave12 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5939 | Slave12 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5940 | Slave12 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5941 | Slave12 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5942 | Slave12 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5943 | Slave12 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5944 | Slave13 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5945 | Slave13 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5946 | Slave13 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5947 | Slave13 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5948 | Slave13 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5949 | Slave13 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5950 | Slave13 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5951 | Slave13 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5952 | Slave14 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5953 | Slave14 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5954 | Slave14 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5955 | Slave14 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5956 | Slave14 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5957 | Slave14 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5958 | Slave14 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5959 | Slave14 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5960 | Slave15 EMD-1 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5961 | Slave15 EMD-2 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5962 | Slave15 EMD-3 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5963 | Slave15 EMD-4 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5964 | Slave15 EMD-5 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5965 | Slave15 EMD-6 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5966 | Slave15 EMD-7 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5967 | Slave15 EMD-8 Valid | RO | 2 bytes | 1:Valid; 0:Invalid
5968 | Master EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5969 | Master EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5970 | Master EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5971 | Master EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5972 | Master EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5973 | Master EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5974 | Master EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5975 | Master EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5976 | Slave01 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5977 | Slave01 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5978 | Slave01 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5979 | Slave01 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5980 | Slave01 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5981 | Slave01 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5982 | Slave01 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5983 | Slave01 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5984 | Slave02 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5985 | Slave02 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5986 | Slave02 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5987 | Slave02 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5988 | Slave02 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5989 | Slave02 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5990 | Slave02 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5991 | Slave02 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
5992 | Slave03 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
5993 | Slave03 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
5994 | Slave03 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
5995 | Slave03 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
5996 | Slave03 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
5997 | Slave03 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
5998 | Slave03 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
5999 | Slave03 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6000 | Slave04 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6001 | Slave04 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6002 | Slave04 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6003 | Slave04 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6004 | Slave04 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6005 | Slave04 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6006 | Slave04 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6007 | Slave04 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6008 | Slave05 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6009 | Slave05 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6010 | Slave05 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6011 | Slave05 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6012 | Slave05 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6013 | Slave05 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6014 | Slave05 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6015 | Slave05 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6016 | Slave06 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6017 | Slave06 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6018 | Slave06 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6019 | Slave06 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6020 | Slave06 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6021 | Slave06 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6022 | Slave06 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6023 | Slave06 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6024 | Slave07 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6025 | Slave07 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6026 | Slave07 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6027 | Slave07 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6028 | Slave07 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6029 | Slave07 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6030 | Slave07 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6031 | Slave07 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6032 | Slave08 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6033 | Slave08 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6034 | Slave08 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6035 | Slave08 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6036 | Slave08 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6037 | Slave08 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6038 | Slave08 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6039 | Slave08 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6040 | Slave09 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6041 | Slave09 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6042 | Slave09 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6043 | Slave09 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6044 | Slave09 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6045 | Slave09 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6046 | Slave09 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6047 | Slave09 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6048 | Slave10 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6049 | Slave10 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6050 | Slave10 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6051 | Slave10 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6052 | Slave10 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6053 | Slave10 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6054 | Slave10 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6055 | Slave10 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6056 | Slave11 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6057 | Slave11 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6058 | Slave11 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6059 | Slave11 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6060 | Slave11 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6061 | Slave11 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6062 | Slave11 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6063 | Slave11 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6064 | Slave12 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6065 | Slave12 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6066 | Slave12 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6067 | Slave12 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6068 | Slave12 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6069 | Slave12 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6070 | Slave12 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6071 | Slave12 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6072 | Slave13 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6073 | Slave13 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6074 | Slave13 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6075 | Slave13 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6076 | Slave13 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6077 | Slave13 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6078 | Slave13 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6079 | Slave13 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6080 | Slave14 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6081 | Slave14 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6082 | Slave14 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6083 | Slave14 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6084 | Slave14 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6085 | Slave14 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6086 | Slave14 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6087 | Slave14 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6088 | Slave15 EMD-1 Temperature | RO | 2 bytes | Unit0.1C
6089 | Slave15 EMD-2 Temperature | RO | 2 bytes | Unit0.1C
6090 | Slave15 EMD-3 Temperature | RO | 2 bytes | Unit0.1C
6091 | Slave15 EMD-4 Temperature | RO | 2 bytes | Unit0.1C
6092 | Slave15 EMD-5 Temperature | RO | 2 bytes | Unit0.1C
6093 | Slave15 EMD-6 Temperature | RO | 2 bytes | Unit0.1C
6094 | Slave15 EMD-7 Temperature | RO | 2 bytes | Unit0.1C
6095 | Slave15 EMD-8 Temperature | RO | 2 bytes | Unit0.1C
6096 | Master EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6097 | Master EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6098 | Master EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6099 | Master EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6100 | Master EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6101 | Master EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6102 | Master EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6103 | Master EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6104 | Slave01 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6105 | Slave01 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6106 | Slave01 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6107 | Slave01 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6108 | Slave01 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6109 | Slave01 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6110 | Slave01 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6111 | Slave01 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6112 | Slave02 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6113 | Slave02 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6114 | Slave02 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6115 | Slave02 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6116 | Slave02 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6117 | Slave02 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6118 | Slave02 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6119 | Slave02 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6120 | Slave03 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6121 | Slave03 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6122 | Slave03 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6123 | Slave03 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6124 | Slave03 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6125 | Slave03 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6126 | Slave03 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6127 | Slave03 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6128 | Slave04 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6129 | Slave04 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6130 | Slave04 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6131 | Slave04 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6132 | Slave04 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6133 | Slave04 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6134 | Slave04 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6135 | Slave04 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6136 | Slave05 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6137 | Slave05 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6138 | Slave05 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6139 | Slave05 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6140 | Slave05 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6141 | Slave05 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6142 | Slave05 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6143 | Slave05 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6144 | Slave06 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6145 | Slave06 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6146 | Slave06 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6147 | Slave06 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6148 | Slave06 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6149 | Slave06 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6150 | Slave06 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6151 | Slave06 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6152 | Slave07 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6153 | Slave07 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6154 | Slave07 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6155 | Slave07 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6156 | Slave07 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6157 | Slave07 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6158 | Slave07 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6159 | Slave07 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6160 | Slave08 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6161 | Slave08 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6162 | Slave08 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6163 | Slave08 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6164 | Slave08 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6165 | Slave08 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6166 | Slave08 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6167 | Slave08 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6168 | Slave09 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6169 | Slave09 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6170 | Slave09 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6171 | Slave09 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6172 | Slave09 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6173 | Slave09 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6174 | Slave09 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6175 | Slave09 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6176 | Slave10 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6177 | Slave10 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6178 | Slave10 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6179 | Slave10 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6180 | Slave10 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6181 | Slave10 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6182 | Slave10 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6183 | Slave10 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6184 | Slave11 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6185 | Slave11 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6186 | Slave11 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6187 | Slave11 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6188 | Slave11 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6189 | Slave11 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6190 | Slave11 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6191 | Slave11 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6192 | Slave12 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6193 | Slave12 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6194 | Slave12 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6195 | Slave12 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6196 | Slave12 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6197 | Slave12 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6198 | Slave12 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6199 | Slave12 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6200 | Slave13 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6201 | Slave13 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6202 | Slave13 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6203 | Slave13 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6204 | Slave13 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6205 | Slave13 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6206 | Slave13 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6207 | Slave13 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6208 | Slave14 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6209 | Slave14 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6210 | Slave14 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6211 | Slave14 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6212 | Slave14 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6213 | Slave14 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6214 | Slave14 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6215 | Slave14 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6216 | Slave15 EMD-1 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6217 | Slave15 EMD-2 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6218 | Slave15 EMD-3 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6219 | Slave15 EMD-4 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6220 | Slave15 EMD-5 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6221 | Slave15 EMD-6 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6222 | Slave15 EMD-7 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6223 | Slave15 EMD-8 Temperature Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6224 | Master EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6225 | Master EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6226 | Master EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6227 | Master EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6228 | Master EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6229 | Master EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6230 | Master EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6231 | Master EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6232 | Slave01 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6233 | Slave01 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6234 | Slave01 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6235 | Slave01 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6236 | Slave01 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6237 | Slave01 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6238 | Slave01 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6239 | Slave01 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6240 | Slave02 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6241 | Slave02 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6242 | Slave02 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6243 | Slave02 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6244 | Slave02 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6245 | Slave02 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6246 | Slave02 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6247 | Slave02 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6248 | Slave03 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6249 | Slave03 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6250 | Slave03 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6251 | Slave03 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6252 | Slave03 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6253 | Slave03 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6254 | Slave03 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6255 | Slave03 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6256 | Slave04 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6257 | Slave04 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6258 | Slave04 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6259 | Slave04 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6260 | Slave04 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6261 | Slave04 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6262 | Slave04 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6263 | Slave04 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6264 | Slave05 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6265 | Slave05 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6266 | Slave05 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6267 | Slave05 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6268 | Slave05 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6269 | Slave05 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6270 | Slave05 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6271 | Slave05 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6272 | Slave06 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6273 | Slave06 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6274 | Slave06 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6275 | Slave06 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6276 | Slave06 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6277 | Slave06 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6278 | Slave06 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6279 | Slave06 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6280 | Slave07 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6281 | Slave07 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6282 | Slave07 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6283 | Slave07 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6284 | Slave07 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6285 | Slave07 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6286 | Slave07 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6287 | Slave07 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6288 | Slave08 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6289 | Slave08 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6290 | Slave08 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6291 | Slave08 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6292 | Slave08 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6293 | Slave08 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6294 | Slave08 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6295 | Slave08 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6296 | Slave09 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6297 | Slave09 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6298 | Slave09 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6299 | Slave09 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6300 | Slave09 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6301 | Slave09 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6302 | Slave09 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6303 | Slave09 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6304 | Slave10 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6305 | Slave10 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6306 | Slave10 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6307 | Slave10 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6308 | Slave10 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6309 | Slave10 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6310 | Slave10 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6311 | Slave10 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6312 | Slave11 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6313 | Slave11 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6314 | Slave11 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6315 | Slave11 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6316 | Slave11 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6317 | Slave11 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6318 | Slave11 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6319 | Slave11 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6320 | Slave12 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6321 | Slave12 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6322 | Slave12 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6323 | Slave12 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6324 | Slave12 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6325 | Slave12 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6326 | Slave12 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6327 | Slave12 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6328 | Slave13 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6329 | Slave13 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6330 | Slave13 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6331 | Slave13 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6332 | Slave13 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6333 | Slave13 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6334 | Slave13 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6335 | Slave13 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6336 | Slave14 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6337 | Slave14 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6338 | Slave14 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6339 | Slave14 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6340 | Slave14 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6341 | Slave14 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6342 | Slave14 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6343 | Slave14 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6344 | Slave15 EMD-1 Humidity | RO | 2 bytes | Unit:0.1%
6345 | Slave15 EMD-2 Humidity | RO | 2 bytes | Unit:0.1%
6346 | Slave15 EMD-3 Humidity | RO | 2 bytes | Unit:0.1%
6347 | Slave15 EMD-4 Humidity | RO | 2 bytes | Unit:0.1%
6348 | Slave15 EMD-5 Humidity | RO | 2 bytes | Unit:0.1%
6349 | Slave15 EMD-6 Humidity | RO | 2 bytes | Unit:0.1%
6350 | Slave15 EMD-7 Humidity | RO | 2 bytes | Unit:0.1%
6351 | Slave15 EMD-8 Humidity | RO | 2 bytes | Unit:0.1%
6352 | Master EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6353 | Master EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6354 | Master EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6355 | Master EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6356 | Master EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6357 | Master EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6358 | Master EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6359 | Master EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6360 | Slave01 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6361 | Slave01 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6362 | Slave01 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6363 | Slave01 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6364 | Slave01 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6365 | Slave01 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6366 | Slave01 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6367 | Slave01 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6368 | Slave02 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6369 | Slave02 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6370 | Slave02 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6371 | Slave02 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6372 | Slave02 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6373 | Slave02 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6374 | Slave02 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6375 | Slave02 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6376 | Slave03 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6377 | Slave03 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6378 | Slave03 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6379 | Slave03 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6380 | Slave03 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6381 | Slave03 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6382 | Slave03 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6383 | Slave03 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6384 | Slave04 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6385 | Slave04 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6386 | Slave04 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6387 | Slave04 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6388 | Slave04 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6389 | Slave04 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6390 | Slave04 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6391 | Slave04 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6392 | Slave05 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6393 | Slave05 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6394 | Slave05 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6395 | Slave05 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6396 | Slave05 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6397 | Slave05 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6398 | Slave05 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6399 | Slave05 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6400 | Slave06 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6401 | Slave06 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6402 | Slave06 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6403 | Slave06 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6404 | Slave06 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6405 | Slave06 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6406 | Slave06 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6407 | Slave06 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6408 | Slave07 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6409 | Slave07 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6410 | Slave07 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6411 | Slave07 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6412 | Slave07 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6413 | Slave07 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6414 | Slave07 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6415 | Slave07 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6416 | Slave08 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6417 | Slave08 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6418 | Slave08 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6419 | Slave08 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6420 | Slave08 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6421 | Slave08 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6422 | Slave08 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6423 | Slave08 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6424 | Slave09 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6425 | Slave09 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6426 | Slave09 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6427 | Slave09 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6428 | Slave09 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6429 | Slave09 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6430 | Slave09 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6431 | Slave09 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6432 | Slave10 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6433 | Slave10 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6434 | Slave10 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6435 | Slave10 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6436 | Slave10 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6437 | Slave10 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6438 | Slave10 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6439 | Slave10 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6440 | Slave11 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6441 | Slave11 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6442 | Slave11 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6443 | Slave11 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6444 | Slave11 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6445 | Slave11 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6446 | Slave11 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6447 | Slave11 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6448 | Slave12 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6449 | Slave12 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6450 | Slave12 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6451 | Slave12 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6452 | Slave12 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6453 | Slave12 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6454 | Slave12 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6455 | Slave12 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6456 | Slave13 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6457 | Slave13 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6458 | Slave13 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6459 | Slave13 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6460 | Slave13 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6461 | Slave13 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6462 | Slave13 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6463 | Slave13 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6464 | Slave14 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6465 | Slave14 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6466 | Slave14 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6467 | Slave14 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6468 | Slave14 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6469 | Slave14 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6470 | Slave14 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6471 | Slave14 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6472 | Slave15 EMD-1 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6473 | Slave15 EMD-2 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6474 | Slave15 EMD-3 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6475 | Slave15 EMD-4 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6476 | Slave15 EMD-5 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6477 | Slave15 EMD-6 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6478 | Slave15 EMD-7 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6479 | Slave15 EMD-8 Humidity Status | RO | 2 bytes | Bit0: Warning; Bit1: Critical; Bit2:High; Bit3:Low
6480 | Master EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6481 | Master EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6482 | Master EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6483 | Master EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6484 | Master EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6485 | Master EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6486 | Master EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6487 | Master EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6488 | Slave01 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6489 | Slave01 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6490 | Slave01 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6491 | Slave01 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6492 | Slave01 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6493 | Slave01 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6494 | Slave01 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6495 | Slave01 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6496 | Slave02 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6497 | Slave02 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6498 | Slave02 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6499 | Slave02 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6500 | Slave02 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6501 | Slave02 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6502 | Slave02 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6503 | Slave02 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6504 | Slave03 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6505 | Slave03 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6506 | Slave03 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6507 | Slave03 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6508 | Slave03 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6509 | Slave03 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6510 | Slave03 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6511 | Slave03 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6512 | Slave04 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6513 | Slave04 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6514 | Slave04 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6515 | Slave04 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6516 | Slave04 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6517 | Slave04 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6518 | Slave04 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6519 | Slave04 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6520 | Slave05 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6521 | Slave05 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6522 | Slave05 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6523 | Slave05 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6524 | Slave05 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6525 | Slave05 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6526 | Slave05 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6527 | Slave05 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6528 | Slave06 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6529 | Slave06 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6530 | Slave06 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6531 | Slave06 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6532 | Slave06 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6533 | Slave06 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6534 | Slave06 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6535 | Slave06 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6536 | Slave07 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6537 | Slave07 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6538 | Slave07 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6539 | Slave07 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6540 | Slave07 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6541 | Slave07 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6542 | Slave07 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6543 | Slave07 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6544 | Slave08 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6545 | Slave08 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6546 | Slave08 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6547 | Slave08 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6548 | Slave08 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6549 | Slave08 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6550 | Slave08 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6551 | Slave08 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6552 | Slave09 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6553 | Slave09 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6554 | Slave09 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6555 | Slave09 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6556 | Slave09 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6557 | Slave09 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6558 | Slave09 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6559 | Slave09 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6560 | Slave10 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6561 | Slave10 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6562 | Slave10 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6563 | Slave10 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6564 | Slave10 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6565 | Slave10 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6566 | Slave10 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6567 | Slave10 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6568 | Slave11 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6569 | Slave11 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6570 | Slave11 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6571 | Slave11 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6572 | Slave11 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6573 | Slave11 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6574 | Slave11 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6575 | Slave11 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6576 | Slave12 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6577 | Slave12 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6578 | Slave12 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6579 | Slave12 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6580 | Slave12 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6581 | Slave12 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6582 | Slave12 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6583 | Slave12 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6584 | Slave13 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6585 | Slave13 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6586 | Slave13 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6587 | Slave13 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6588 | Slave13 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6589 | Slave13 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6590 | Slave13 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6591 | Slave13 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6592 | Slave14 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6593 | Slave14 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6594 | Slave14 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6595 | Slave14 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6596 | Slave14 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6597 | Slave14 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6598 | Slave14 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6599 | Slave14 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6600 | Slave15 EMD-1 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6601 | Slave15 EMD-2 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6602 | Slave15 EMD-3 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6603 | Slave15 EMD-4 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6604 | Slave15 EMD-5 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6605 | Slave15 EMD-6 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6606 | Slave15 EMD-7 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6607 | Slave15 EMD-8 Alarm1 | RO | 2 bytes | 0:invalid; 1:normal; 2:alarm
6608 | Master EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6609 | Master EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6610 | Master EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6611 | Master EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6612 | Master EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6613 | Master EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6614 | Master EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6615 | Master EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6616 | Slave01 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6617 | Slave01 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6618 | Slave01 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6619 | Slave01 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6620 | Slave01 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6621 | Slave01 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6622 | Slave01 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6623 | Slave01 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6624 | Slave02 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6625 | Slave02 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6626 | Slave02 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6627 | Slave02 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6628 | Slave02 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6629 | Slave02 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6630 | Slave02 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6631 | Slave02 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6632 | Slave03 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6633 | Slave03 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6634 | Slave03 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6635 | Slave03 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6636 | Slave03 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6637 | Slave03 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6638 | Slave03 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6639 | Slave03 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6640 | Slave04 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6641 | Slave04 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6642 | Slave04 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6643 | Slave04 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6644 | Slave04 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6645 | Slave04 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6646 | Slave04 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6647 | Slave04 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6648 | Slave05 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6649 | Slave05 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6650 | Slave05 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6651 | Slave05 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6652 | Slave05 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6653 | Slave05 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6654 | Slave05 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6655 | Slave05 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6656 | Slave06 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6657 | Slave06 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6658 | Slave06 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6659 | Slave06 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6660 | Slave06 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6661 | Slave06 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6662 | Slave06 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6663 | Slave06 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6664 | Slave07 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6665 | Slave07 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6666 | Slave07 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6667 | Slave07 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6668 | Slave07 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6669 | Slave07 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6670 | Slave07 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6671 | Slave07 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6672 | Slave08 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6673 | Slave08 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6674 | Slave08 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6675 | Slave08 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6676 | Slave08 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6677 | Slave08 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6678 | Slave08 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6679 | Slave08 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6680 | Slave09 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6681 | Slave09 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6682 | Slave09 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6683 | Slave09 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6684 | Slave09 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6685 | Slave09 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6686 | Slave09 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6687 | Slave09 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6688 | Slave10 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6689 | Slave10 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6690 | Slave10 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6691 | Slave10 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6692 | Slave10 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6693 | Slave10 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6694 | Slave10 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6695 | Slave10 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6696 | Slave11 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6697 | Slave11 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6698 | Slave11 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6699 | Slave11 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6700 | Slave11 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6701 | Slave11 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6702 | Slave11 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6703 | Slave11 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6704 | Slave12 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6705 | Slave12 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6706 | Slave12 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6707 | Slave12 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6708 | Slave12 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6709 | Slave12 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6710 | Slave12 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6711 | Slave12 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6712 | Slave13 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6713 | Slave13 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6714 | Slave13 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6715 | Slave13 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6716 | Slave13 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6717 | Slave13 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6718 | Slave13 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6719 | Slave13 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6720 | Slave14 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6721 | Slave14 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6722 | Slave14 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6723 | Slave14 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6724 | Slave14 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6725 | Slave14 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6726 | Slave14 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6727 | Slave14 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6728 | Slave15 EMD-1 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6729 | Slave15 EMD-2 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6730 | Slave15 EMD-3 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6731 | Slave15 EMD-4 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6732 | Slave15 EMD-5 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6733 | Slave15 EMD-6 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6734 | Slave15 EMD-7 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6735 | Slave15 EMD-8 Alarm2 | RO | 2 bytes | :invalid; 1:normal; 2:alarm
6736 | Master Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6738 | Slave01 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6740 | Slave02 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6742 | Slave03 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6744 | Slave04 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6746 | Slave05 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6748 | Slave06 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6750 | Slave07 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6752 | Slave08 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6754 | Slave09 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6756 | Slave10 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6758 | Slave11 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6760 | Slave12 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6762 | Slave13 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6764 | Slave14 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6766 | Slave15 Inlet Phase1 Active Power | RO | 4 bytes | Unit:0.1
6768 | Master Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6770 | Slave01 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6772 | Slave02 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6774 | Slave03 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6776 | Slave04 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6778 | Slave05 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6780 | Slave06 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6782 | Slave07 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6784 | Slave08 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6786 | Slave09 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6788 | Slave10 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6790 | Slave11 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6792 | Slave12 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6794 | Slave13 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6796 | Slave14 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6798 | Slave15 Inlet Phase2 Active Power | RO | 4 bytes | Unit:0.1
6800 | Master Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6802 | Slave01 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6804 | Slave02 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6806 | Slave03 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6808 | Slave04 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6810 | Slave05 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6812 | Slave06 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6814 | Slave07 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6816 | Slave08 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6818 | Slave09 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6820 | Slave10 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6822 | Slave11 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6824 | Slave12 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6826 | Slave13 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6828 | Slave14 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6830 | Slave15 Inlet Phase3 Active Power | RO | 4 bytes | Unit:0.1
6832 | Master Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6834 | Slave01 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6836 | Slave02 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6838 | Slave03 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6840 | Slave04 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6842 | Slave05 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6844 | Slave06 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6846 | Slave07 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6848 | Slave08 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6850 | Slave09 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6852 | Slave10 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6854 | Slave11 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6856 | Slave12 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6858 | Slave13 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6860 | Slave14 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6862 | Slave15 Inlet Phase1 Apparent Power | RO | 4 bytes | Unit:0.1
6864 | Master Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6866 | Slave01 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6868 | Slave02 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6870 | Slave03 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6872 | Slave04 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6874 | Slave05 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6876 | Slave06 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6878 | Slave07 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6880 | Slave08 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6882 | Slave09 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6884 | Slave10 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6886 | Slave11 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6888 | Slave12 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6890 | Slave13 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6892 | Slave14 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6894 | Slave15 Inlet Phase2 Apparent Power | RO | 4 bytes | Unit:0.1
6896 | Master Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6898 | Slave01 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6900 | Slave02 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6902 | Slave03 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6904 | Slave04 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6906 | Slave05 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6908 | Slave06 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6910 | Slave07 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6912 | Slave08 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6914 | Slave09 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6916 | Slave10 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6918 | Slave11 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6920 | Slave12 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6922 | Slave13 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6924 | Slave14 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6926 | Slave15 Inlet Phase3 Apparent Power | RO | 4 bytes | Unit:0.1
6928 | Master Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6930 | Slave01 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6932 | Slave02 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6934 | Slave03 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6936 | Slave04 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6938 | Slave05 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6940 | Slave06 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6942 | Slave07 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6944 | Slave08 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6946 | Slave09 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6948 | Slave10 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6950 | Slave11 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6952 | Slave12 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6954 | Slave13 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6956 | Slave14 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6958 | Slave15 Inlet Phase1 Reactive Power | RO | 4 bytes | Unit:0.1
6960 | Master Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6962 | Slave01 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6964 | Slave02 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6966 | Slave03 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6968 | Slave04 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6970 | Slave05 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6972 | Slave06 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6974 | Slave07 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6976 | Slave08 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6978 | Slave09 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6980 | Slave10 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6982 | Slave11 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6984 | Slave12 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6986 | Slave13 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6988 | Slave14 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6990 | Slave15 Inlet Phase2 Reactive Power | RO | 4 bytes | Unit:0.1
6992 | Master Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6994 | Slave01 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6996 | Slave02 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
6998 | Slave03 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7000 | Slave04 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7002 | Slave05 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7004 | Slave06 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7006 | Slave07 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7008 | Slave08 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7010 | Slave09 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7012 | Slave10 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7014 | Slave11 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7016 | Slave12 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7018 | Slave13 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7020 | Slave14 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7022 | Slave15 Inlet Phase3 Reactive Power | RO | 4 bytes | Unit:0.1
7024 | Master Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7026 | Slave01 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7028 | Slave02 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7030 | Slave03 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7032 | Slave04 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7034 | Slave05 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7036 | Slave06 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7038 | Slave07 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7040 | Slave08 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7042 | Slave09 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7044 | Slave10 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7046 | Slave11 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7048 | Slave12 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7050 | Slave13 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7052 | Slave14 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7054 | Slave15 Inlet Phase1 Energy | RO | 4 bytes | Unit:0.001KW
7056 | Master Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7058 | Slave01 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7060 | Slave02 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7062 | Slave03 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7064 | Slave04 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7066 | Slave05 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7068 | Slave06 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7070 | Slave07 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7072 | Slave08 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7074 | Slave09 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7076 | Slave10 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7078 | Slave11 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7080 | Slave12 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7082 | Slave13 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7084 | Slave14 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7086 | Slave15 Inlet Phase2 Energy | RO | 4 bytes | Unit:0.001KW
7088 | Master Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7090 | Slave01 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7092 | Slave02 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7094 | Slave03 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7096 | Slave04 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7098 | Slave05 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7100 | Slave06 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7102 | Slave07 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7104 | Slave08 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7106 | Slave09 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7108 | Slave10 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7110 | Slave11 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7112 | Slave12 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7114 | Slave13 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7116 | Slave14 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7118 | Slave15 Inlet Phase3 Energy | RO | 4 bytes | Unit:0.001KW
7120 | Master Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7122 | Slave01 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7124 | Slave02 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7126 | Slave03 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7128 | Slave04 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7130 | Slave05 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7132 | Slave06 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7134 | Slave07 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7136 | Slave08 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7138 | Slave09 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7140 | Slave10 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7142 | Slave11 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7144 | Slave12 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7146 | Slave13 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7148 | Slave14 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7150 | Slave15 Inlet Total Energy | RO | 4 bytes | Unit:0.001KW
7152 | Master Inlet Load Balance | RO | 4 bytes | Unit:1
7154 | Slave01 Inlet Load Balance | RO | 4 bytes | Unit:1
7156 | Slave02 Inlet Load Balance | RO | 4 bytes | Unit:1
7158 | Slave03 Inlet Load Balance | RO | 4 bytes | Unit:1
7160 | Slave04 Inlet Load Balance | RO | 4 bytes | Unit:1
7162 | Slave05 Inlet Load Balance | RO | 4 bytes | Unit:1
7164 | Slave06 Inlet Load Balance | RO | 4 bytes | Unit:1
7166 | Slave07 Inlet Load Balance | RO | 4 bytes | Unit:1
7168 | Slave08 Inlet Load Balance | RO | 4 bytes | Unit:1
7170 | Slave09 Inlet Load Balance | RO | 4 bytes | Unit:1
7172 | Slave10 Inlet Load Balance | RO | 4 bytes | Unit:1
7174 | Slave11 Inlet Load Balance | RO | 4 bytes | Unit:1
7176 | Slave12 Inlet Load Balance | RO | 4 bytes | Unit:1
7178 | Slave13 Inlet Load Balance | RO | 4 bytes | Unit:1
7180 | Slave14 Inlet Load Balance | RO | 4 bytes | Unit:1
7182 | Slave15 Inlet Load Balance | RO | 4 bytes | Unit:1
7184 | Master Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7186 | Master Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7188 | Master Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7190 | Master Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7192 | Master Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7194 | Master Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7196 | Master Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7198 | Master Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7200 | Master Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7202 | Master Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7204 | Master Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7206 | Master Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7208 | Master Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7210 | Master Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7212 | Master Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7214 | Master Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7216 | Master Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7218 | Master Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7220 | Master Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7222 | Master Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7224 | Master Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7226 | Master Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7228 | Master Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7230 | Master Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7232 | Master Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7234 | Master Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7236 | Master Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7238 | Master Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7240 | Master Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7242 | Master Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7244 | Master Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7246 | Master Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7248 | Master Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7250 | Master Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7252 | Master Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7254 | Master Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7256 | Master Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7258 | Master Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7260 | Master Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7262 | Master Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7264 | Master Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7266 | Master Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7268 | Master Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7270 | Master Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7272 | Master Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7274 | Master Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7276 | Master Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7278 | Master Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7280 | Slave01 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7282 | Slave01 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7284 | Slave01 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7286 | Slave01 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7288 | Slave01 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7290 | Slave01 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7292 | Slave01 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7294 | Slave01 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7296 | Slave01 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7298 | Slave01 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7300 | Slave01 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7302 | Slave01 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7304 | Slave01 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7306 | Slave01 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7308 | Slave01 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7310 | Slave01 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7312 | Slave01 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7314 | Slave01 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7316 | Slave01 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7318 | Slave01 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7320 | Slave01 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7322 | Slave01 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7324 | Slave01 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7326 | Slave01 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7328 | Slave01 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7330 | Slave01 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7332 | Slave01 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7334 | Slave01 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7336 | Slave01 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7338 | Slave01 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7340 | Slave01 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7342 | Slave01 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7344 | Slave01 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7346 | Slave01 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7348 | Slave01 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7350 | Slave01 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7352 | Slave01 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7354 | Slave01 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7356 | Slave01 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7358 | Slave01 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7360 | Slave01 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7362 | Slave01 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7364 | Slave01 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7366 | Slave01 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7368 | Slave01 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7370 | Slave01 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7372 | Slave01 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7374 | Slave01 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7376 | Slave02 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7378 | Slave02 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7380 | Slave02 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7382 | Slave02 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7384 | Slave02 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7386 | Slave02 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7388 | Slave02 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7390 | Slave02 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7392 | Slave02 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7394 | Slave02 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7396 | Slave02 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7398 | Slave02 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7400 | Slave02 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7402 | Slave02 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7404 | Slave02 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7406 | Slave02 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7408 | Slave02 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7410 | Slave02 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7412 | Slave02 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7414 | Slave02 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7416 | Slave02 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7418 | Slave02 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7420 | Slave02 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7422 | Slave02 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7424 | Slave02 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7426 | Slave02 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7428 | Slave02 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7430 | Slave02 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7432 | Slave02 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7434 | Slave02 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7436 | Slave02 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7438 | Slave02 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7440 | Slave02 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7442 | Slave02 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7444 | Slave02 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7446 | Slave02 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7448 | Slave02 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7450 | Slave02 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7452 | Slave02 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7454 | Slave02 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7456 | Slave02 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7458 | Slave02 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7460 | Slave02 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7462 | Slave02 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7464 | Slave02 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7466 | Slave02 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7468 | Slave02 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7470 | Slave02 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7472 | Slave03 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7474 | Slave03 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7476 | Slave03 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7478 | Slave03 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7480 | Slave03 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7482 | Slave03 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7484 | Slave03 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7486 | Slave03 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7488 | Slave03 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7490 | Slave03 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7492 | Slave03 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7494 | Slave03 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7496 | Slave03 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7498 | Slave03 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7500 | Slave03 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7502 | Slave03 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7504 | Slave03 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7506 | Slave03 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7508 | Slave03 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7510 | Slave03 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7512 | Slave03 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7514 | Slave03 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7516 | Slave03 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7518 | Slave03 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7520 | Slave03 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7522 | Slave03 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7524 | Slave03 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7526 | Slave03 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7528 | Slave03 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7530 | Slave03 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7532 | Slave03 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7534 | Slave03 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7536 | Slave03 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7538 | Slave03 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7540 | Slave03 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7542 | Slave03 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7544 | Slave03 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7546 | Slave03 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7548 | Slave03 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7550 | Slave03 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7552 | Slave03 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7554 | Slave03 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7556 | Slave03 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7558 | Slave03 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7560 | Slave03 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7562 | Slave03 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7564 | Slave03 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7566 | Slave03 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7568 | Slave04 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7570 | Slave04 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7572 | Slave04 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7574 | Slave04 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7576 | Slave04 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7578 | Slave04 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7580 | Slave04 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7582 | Slave04 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7584 | Slave04 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7586 | Slave04 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7588 | Slave04 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7590 | Slave04 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7592 | Slave04 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7594 | Slave04 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7596 | Slave04 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7598 | Slave04 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7600 | Slave04 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7602 | Slave04 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7604 | Slave04 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7606 | Slave04 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7608 | Slave04 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7610 | Slave04 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7612 | Slave04 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7614 | Slave04 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7616 | Slave04 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7618 | Slave04 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7620 | Slave04 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7622 | Slave04 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7624 | Slave04 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7626 | Slave04 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7628 | Slave04 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7630 | Slave04 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7632 | Slave04 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7634 | Slave04 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7636 | Slave04 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7638 | Slave04 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7640 | Slave04 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7642 | Slave04 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7644 | Slave04 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7646 | Slave04 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7648 | Slave04 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7650 | Slave04 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7652 | Slave04 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7654 | Slave04 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7656 | Slave04 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7658 | Slave04 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7660 | Slave04 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7662 | Slave04 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7664 | Slave05 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7666 | Slave05 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7668 | Slave05 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7670 | Slave05 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7672 | Slave05 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7674 | Slave05 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7676 | Slave05 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7678 | Slave05 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7680 | Slave05 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7682 | Slave05 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7684 | Slave05 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7686 | Slave05 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7688 | Slave05 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7690 | Slave05 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7692 | Slave05 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7694 | Slave05 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7696 | Slave05 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7698 | Slave05 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7700 | Slave05 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7702 | Slave05 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7704 | Slave05 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7706 | Slave05 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7708 | Slave05 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7710 | Slave05 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7712 | Slave05 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7714 | Slave05 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7716 | Slave05 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7718 | Slave05 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7720 | Slave05 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7722 | Slave05 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7724 | Slave05 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7726 | Slave05 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7728 | Slave05 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7730 | Slave05 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7732 | Slave05 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7734 | Slave05 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7736 | Slave05 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7738 | Slave05 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7740 | Slave05 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7742 | Slave05 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7744 | Slave05 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7746 | Slave05 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7748 | Slave05 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7750 | Slave05 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7752 | Slave05 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7754 | Slave05 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7756 | Slave05 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7758 | Slave05 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7760 | Slave06 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7762 | Slave06 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7764 | Slave06 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7766 | Slave06 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7768 | Slave06 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7770 | Slave06 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7772 | Slave06 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7774 | Slave06 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7776 | Slave06 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7778 | Slave06 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7780 | Slave06 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7782 | Slave06 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7784 | Slave06 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7786 | Slave06 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7788 | Slave06 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7790 | Slave06 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7792 | Slave06 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7794 | Slave06 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7796 | Slave06 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7798 | Slave06 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7800 | Slave06 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7802 | Slave06 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7804 | Slave06 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7806 | Slave06 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7808 | Slave06 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7810 | Slave06 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7812 | Slave06 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7814 | Slave06 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7816 | Slave06 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7818 | Slave06 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7820 | Slave06 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7822 | Slave06 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7824 | Slave06 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7826 | Slave06 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7828 | Slave06 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7830 | Slave06 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7832 | Slave06 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7834 | Slave06 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7836 | Slave06 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7838 | Slave06 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7840 | Slave06 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7842 | Slave06 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7844 | Slave06 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7846 | Slave06 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7848 | Slave06 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7850 | Slave06 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7852 | Slave06 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7854 | Slave06 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7856 | Slave07 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7858 | Slave07 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7860 | Slave07 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7862 | Slave07 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7864 | Slave07 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7866 | Slave07 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7868 | Slave07 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7870 | Slave07 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7872 | Slave07 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7874 | Slave07 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7876 | Slave07 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7878 | Slave07 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7880 | Slave07 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7882 | Slave07 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7884 | Slave07 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7886 | Slave07 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7888 | Slave07 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7890 | Slave07 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7892 | Slave07 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7894 | Slave07 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7896 | Slave07 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7898 | Slave07 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7900 | Slave07 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7902 | Slave07 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
7904 | Slave07 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
7906 | Slave07 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
7908 | Slave07 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
7910 | Slave07 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
7912 | Slave07 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
7914 | Slave07 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
7916 | Slave07 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
7918 | Slave07 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
7920 | Slave07 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
7922 | Slave07 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
7924 | Slave07 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
7926 | Slave07 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
7928 | Slave07 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
7930 | Slave07 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
7932 | Slave07 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
7934 | Slave07 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
7936 | Slave07 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
7938 | Slave07 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
7940 | Slave07 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
7942 | Slave07 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
7944 | Slave07 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
7946 | Slave07 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
7948 | Slave07 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
7950 | Slave07 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
7952 | Slave08 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
7954 | Slave08 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
7956 | Slave08 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
7958 | Slave08 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
7960 | Slave08 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
7962 | Slave08 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
7964 | Slave08 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
7966 | Slave08 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
7968 | Slave08 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
7970 | Slave08 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
7972 | Slave08 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
7974 | Slave08 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
7976 | Slave08 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
7978 | Slave08 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
7980 | Slave08 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
7982 | Slave08 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
7984 | Slave08 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
7986 | Slave08 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
7988 | Slave08 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
7990 | Slave08 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
7992 | Slave08 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
7994 | Slave08 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
7996 | Slave08 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
7998 | Slave08 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8000 | Slave08 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8002 | Slave08 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8004 | Slave08 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8006 | Slave08 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8008 | Slave08 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8010 | Slave08 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8012 | Slave08 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8014 | Slave08 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8016 | Slave08 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8018 | Slave08 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8020 | Slave08 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8022 | Slave08 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8024 | Slave08 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8026 | Slave08 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8028 | Slave08 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8030 | Slave08 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8032 | Slave08 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8034 | Slave08 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8036 | Slave08 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8038 | Slave08 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8040 | Slave08 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8042 | Slave08 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8044 | Slave08 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8046 | Slave08 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8048 | Slave09 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8050 | Slave09 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8052 | Slave09 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8054 | Slave09 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8056 | Slave09 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8058 | Slave09 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8060 | Slave09 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8062 | Slave09 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8064 | Slave09 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8066 | Slave09 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8068 | Slave09 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8070 | Slave09 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8072 | Slave09 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8074 | Slave09 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8076 | Slave09 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8078 | Slave09 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8080 | Slave09 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8082 | Slave09 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8084 | Slave09 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8086 | Slave09 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8088 | Slave09 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8090 | Slave09 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8092 | Slave09 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8094 | Slave09 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8096 | Slave09 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8098 | Slave09 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8100 | Slave09 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8102 | Slave09 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8104 | Slave09 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8106 | Slave09 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8108 | Slave09 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8110 | Slave09 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8112 | Slave09 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8114 | Slave09 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8116 | Slave09 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8118 | Slave09 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8120 | Slave09 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8122 | Slave09 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8124 | Slave09 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8126 | Slave09 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8128 | Slave09 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8130 | Slave09 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8132 | Slave09 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8134 | Slave09 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8136 | Slave09 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8138 | Slave09 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8140 | Slave09 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8142 | Slave09 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8144 | Slave10 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8146 | Slave10 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8148 | Slave10 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8150 | Slave10 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8152 | Slave10 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8154 | Slave10 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8156 | Slave10 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8158 | Slave10 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8160 | Slave10 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8162 | Slave10 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8164 | Slave10 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8166 | Slave10 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8168 | Slave10 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8170 | Slave10 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8172 | Slave10 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8174 | Slave10 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8176 | Slave10 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8178 | Slave10 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8180 | Slave10 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8182 | Slave10 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8184 | Slave10 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8186 | Slave10 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8188 | Slave10 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8190 | Slave10 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8192 | Slave10 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8194 | Slave10 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8196 | Slave10 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8198 | Slave10 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8200 | Slave10 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8202 | Slave10 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8204 | Slave10 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8206 | Slave10 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8208 | Slave10 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8210 | Slave10 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8212 | Slave10 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8214 | Slave10 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8216 | Slave10 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8218 | Slave10 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8220 | Slave10 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8222 | Slave10 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8224 | Slave10 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8226 | Slave10 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8228 | Slave10 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8230 | Slave10 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8232 | Slave10 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8234 | Slave10 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8236 | Slave10 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8238 | Slave10 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8240 | Slave11 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8242 | Slave11 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8244 | Slave11 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8246 | Slave11 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8248 | Slave11 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8250 | Slave11 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8252 | Slave11 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8254 | Slave11 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8256 | Slave11 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8258 | Slave11 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8260 | Slave11 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8262 | Slave11 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8264 | Slave11 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8266 | Slave11 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8268 | Slave11 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8270 | Slave11 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8272 | Slave11 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8274 | Slave11 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8276 | Slave11 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8278 | Slave11 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8280 | Slave11 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8282 | Slave11 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8284 | Slave11 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8286 | Slave11 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8288 | Slave11 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8290 | Slave11 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8292 | Slave11 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8294 | Slave11 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8296 | Slave11 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8298 | Slave11 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8300 | Slave11 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8302 | Slave11 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8304 | Slave11 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8306 | Slave11 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8308 | Slave11 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8310 | Slave11 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8312 | Slave11 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8314 | Slave11 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8316 | Slave11 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8318 | Slave11 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8320 | Slave11 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8322 | Slave11 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8324 | Slave11 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8326 | Slave11 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8328 | Slave11 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8330 | Slave11 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8332 | Slave11 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8334 | Slave11 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8336 | Slave12 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8338 | Slave12 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8340 | Slave12 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8342 | Slave12 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8344 | Slave12 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8346 | Slave12 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8348 | Slave12 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8350 | Slave12 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8352 | Slave12 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8354 | Slave12 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8356 | Slave12 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8358 | Slave12 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8360 | Slave12 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8362 | Slave12 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8364 | Slave12 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8366 | Slave12 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8368 | Slave12 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8370 | Slave12 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8372 | Slave12 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8374 | Slave12 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8376 | Slave12 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8378 | Slave12 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8380 | Slave12 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8382 | Slave12 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8384 | Slave12 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8386 | Slave12 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8388 | Slave12 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8390 | Slave12 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8392 | Slave12 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8394 | Slave12 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8396 | Slave12 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8398 | Slave12 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8400 | Slave12 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8402 | Slave12 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8404 | Slave12 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8406 | Slave12 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8408 | Slave12 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8410 | Slave12 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8412 | Slave12 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8414 | Slave12 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8416 | Slave12 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8418 | Slave12 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8420 | Slave12 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8422 | Slave12 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8424 | Slave12 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8426 | Slave12 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8428 | Slave12 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8430 | Slave12 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8432 | Slave13 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8434 | Slave13 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8436 | Slave13 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8438 | Slave13 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8440 | Slave13 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8442 | Slave13 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8444 | Slave13 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8446 | Slave13 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8448 | Slave13 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8450 | Slave13 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8452 | Slave13 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8454 | Slave13 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8456 | Slave13 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8458 | Slave13 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8460 | Slave13 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8462 | Slave13 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8464 | Slave13 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8466 | Slave13 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8468 | Slave13 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8470 | Slave13 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8472 | Slave13 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8474 | Slave13 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8476 | Slave13 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8478 | Slave13 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8480 | Slave13 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8482 | Slave13 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8484 | Slave13 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8486 | Slave13 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8488 | Slave13 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8490 | Slave13 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8492 | Slave13 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8494 | Slave13 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8496 | Slave13 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8498 | Slave13 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8500 | Slave13 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8502 | Slave13 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8504 | Slave13 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8506 | Slave13 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8508 | Slave13 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8510 | Slave13 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8512 | Slave13 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8514 | Slave13 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8516 | Slave13 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8518 | Slave13 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8520 | Slave13 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8522 | Slave13 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8524 | Slave13 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8526 | Slave13 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8528 | Slave14 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8530 | Slave14 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8532 | Slave14 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8534 | Slave14 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8536 | Slave14 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8538 | Slave14 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8540 | Slave14 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8542 | Slave14 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8544 | Slave14 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8546 | Slave14 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8548 | Slave14 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8550 | Slave14 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8552 | Slave14 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8554 | Slave14 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8556 | Slave14 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8558 | Slave14 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8560 | Slave14 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8562 | Slave14 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8564 | Slave14 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8566 | Slave14 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8568 | Slave14 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8570 | Slave14 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8572 | Slave14 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8574 | Slave14 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8576 | Slave14 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8578 | Slave14 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8580 | Slave14 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8582 | Slave14 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8584 | Slave14 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8586 | Slave14 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8588 | Slave14 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8590 | Slave14 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8592 | Slave14 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8594 | Slave14 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8596 | Slave14 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8598 | Slave14 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8600 | Slave14 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8602 | Slave14 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8604 | Slave14 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8606 | Slave14 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8608 | Slave14 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8610 | Slave14 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8612 | Slave14 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8614 | Slave14 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8616 | Slave14 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8618 | Slave14 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8620 | Slave14 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8622 | Slave14 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8624 | Slave15 Outlet Port01 Active Power | RO | 4 bytes | Unit:0.1
8626 | Slave15 Outlet Port02 Active Power | RO | 4 bytes | Unit:0.1
8628 | Slave15 Outlet Port03 Active Power | RO | 4 bytes | Unit:0.1
8630 | Slave15 Outlet Port04 Active Power | RO | 4 bytes | Unit:0.1
8632 | Slave15 Outlet Port05 Active Power | RO | 4 bytes | Unit:0.1
8634 | Slave15 Outlet Port06 Active Power | RO | 4 bytes | Unit:0.1
8636 | Slave15 Outlet Port07 Active Power | RO | 4 bytes | Unit:0.1
8638 | Slave15 Outlet Port08 Active Power | RO | 4 bytes | Unit:0.1
8640 | Slave15 Outlet Port09 Active Power | RO | 4 bytes | Unit:0.1
8642 | Slave15 Outlet Port10 Active Power | RO | 4 bytes | Unit:0.1
8644 | Slave15 Outlet Port11 Active Power | RO | 4 bytes | Unit:0.1
8646 | Slave15 Outlet Port12 Active Power | RO | 4 bytes | Unit:0.1
8648 | Slave15 Outlet Port13 Active Power | RO | 4 bytes | Unit:0.1
8650 | Slave15 Outlet Port14 Active Power | RO | 4 bytes | Unit:0.1
8652 | Slave15 Outlet Port15 Active Power | RO | 4 bytes | Unit:0.1
8654 | Slave15 Outlet Port16 Active Power | RO | 4 bytes | Unit:0.1
8656 | Slave15 Outlet Port17 Active Power | RO | 4 bytes | Unit:0.1
8658 | Slave15 Outlet Port18 Active Power | RO | 4 bytes | Unit:0.1
8660 | Slave15 Outlet Port19 Active Power | RO | 4 bytes | Unit:0.1
8662 | Slave15 Outlet Port20 Active Power | RO | 4 bytes | Unit:0.1
8664 | Slave15 Outlet Port21 Active Power | RO | 4 bytes | Unit:0.1
8666 | Slave15 Outlet Port22 Active Power | RO | 4 bytes | Unit:0.1
8668 | Slave15 Outlet Port23 Active Power | RO | 4 bytes | Unit:0.1
8670 | Slave15 Outlet Port24 Active Power | RO | 4 bytes | Unit:0.1
8672 | Slave15 Outlet Port25 Active Power | RO | 4 bytes | Unit:0.1
8674 | Slave15 Outlet Port26 Active Power | RO | 4 bytes | Unit:0.1
8676 | Slave15 Outlet Port27 Active Power | RO | 4 bytes | Unit:0.1
8678 | Slave15 Outlet Port28 Active Power | RO | 4 bytes | Unit:0.1
8680 | Slave15 Outlet Port29 Active Power | RO | 4 bytes | Unit:0.1
8682 | Slave15 Outlet Port30 Active Power | RO | 4 bytes | Unit:0.1
8684 | Slave15 Outlet Port31 Active Power | RO | 4 bytes | Unit:0.1
8686 | Slave15 Outlet Port32 Active Power | RO | 4 bytes | Unit:0.1
8688 | Slave15 Outlet Port33 Active Power | RO | 4 bytes | Unit:0.1
8690 | Slave15 Outlet Port34 Active Power | RO | 4 bytes | Unit:0.1
8692 | Slave15 Outlet Port35 Active Power | RO | 4 bytes | Unit:0.1
8694 | Slave15 Outlet Port36 Active Power | RO | 4 bytes | Unit:0.1
8696 | Slave15 Outlet Port37 Active Power | RO | 4 bytes | Unit:0.1
8698 | Slave15 Outlet Port38 Active Power | RO | 4 bytes | Unit:0.1
8700 | Slave15 Outlet Port39 Active Power | RO | 4 bytes | Unit:0.1
8702 | Slave15 Outlet Port40 Active Power | RO | 4 bytes | Unit:0.1
8704 | Slave15 Outlet Port41 Active Power | RO | 4 bytes | Unit:0.1
8706 | Slave15 Outlet Port42 Active Power | RO | 4 bytes | Unit:0.1
8708 | Slave15 Outlet Port43 Active Power | RO | 4 bytes | Unit:0.1
8710 | Slave15 Outlet Port44 Active Power | RO | 4 bytes | Unit:0.1
8712 | Slave15 Outlet Port45 Active Power | RO | 4 bytes | Unit:0.1
8714 | Slave15 Outlet Port46 Active Power | RO | 4 bytes | Unit:0.1
8716 | Slave15 Outlet Port47 Active Power | RO | 4 bytes | Unit:0.1
8718 | Slave15 Outlet Port48 Active Power | RO | 4 bytes | Unit:0.1
8720 | Master Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8722 | Master Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8724 | Master Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8726 | Master Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8728 | Master Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8730 | Master Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8732 | Master Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8734 | Master Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8736 | Master Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8738 | Master Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8740 | Master Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8742 | Master Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8744 | Master Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8746 | Master Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8748 | Master Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8750 | Master Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8752 | Master Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8754 | Master Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8756 | Master Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8758 | Master Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8760 | Master Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8762 | Master Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8764 | Master Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8766 | Master Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8768 | Master Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8770 | Master Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8772 | Master Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8774 | Master Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8776 | Master Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8778 | Master Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8780 | Master Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8782 | Master Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8784 | Master Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8786 | Master Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8788 | Master Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8790 | Master Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8792 | Master Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8794 | Master Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8796 | Master Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8798 | Master Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8800 | Master Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8802 | Master Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8804 | Master Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
8806 | Master Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
8808 | Master Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
8810 | Master Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
8812 | Master Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
8814 | Master Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
8816 | Slave01 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8818 | Slave01 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8820 | Slave01 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8822 | Slave01 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8824 | Slave01 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8826 | Slave01 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8828 | Slave01 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8830 | Slave01 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8832 | Slave01 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8834 | Slave01 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8836 | Slave01 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8838 | Slave01 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8840 | Slave01 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8842 | Slave01 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8844 | Slave01 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8846 | Slave01 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8848 | Slave01 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8850 | Slave01 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8852 | Slave01 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8854 | Slave01 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8856 | Slave01 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8858 | Slave01 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8860 | Slave01 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8862 | Slave01 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8864 | Slave01 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8866 | Slave01 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8868 | Slave01 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8870 | Slave01 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8872 | Slave01 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8874 | Slave01 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8876 | Slave01 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8878 | Slave01 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8880 | Slave01 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8882 | Slave01 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8884 | Slave01 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8886 | Slave01 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8888 | Slave01 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8890 | Slave01 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8892 | Slave01 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8894 | Slave01 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8896 | Slave01 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8898 | Slave01 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8900 | Slave01 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
8902 | Slave01 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
8904 | Slave01 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
8906 | Slave01 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
8908 | Slave01 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
8910 | Slave01 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
8912 | Slave02 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
8914 | Slave02 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
8916 | Slave02 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
8918 | Slave02 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
8920 | Slave02 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
8922 | Slave02 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
8924 | Slave02 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
8926 | Slave02 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
8928 | Slave02 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
8930 | Slave02 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
8932 | Slave02 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
8934 | Slave02 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
8936 | Slave02 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
8938 | Slave02 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
8940 | Slave02 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
8942 | Slave02 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
8944 | Slave02 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
8946 | Slave02 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
8948 | Slave02 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
8950 | Slave02 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
8952 | Slave02 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
8954 | Slave02 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
8956 | Slave02 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
8958 | Slave02 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
8960 | Slave02 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
8962 | Slave02 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
8964 | Slave02 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
8966 | Slave02 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
8968 | Slave02 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
8970 | Slave02 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
8972 | Slave02 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
8974 | Slave02 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
8976 | Slave02 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
8978 | Slave02 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
8980 | Slave02 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
8982 | Slave02 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
8984 | Slave02 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
8986 | Slave02 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
8988 | Slave02 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
8990 | Slave02 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
8992 | Slave02 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
8994 | Slave02 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
8996 | Slave02 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
8998 | Slave02 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9000 | Slave02 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9002 | Slave02 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9004 | Slave02 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9006 | Slave02 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9008 | Slave03 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9010 | Slave03 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9012 | Slave03 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9014 | Slave03 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9016 | Slave03 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9018 | Slave03 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9020 | Slave03 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9022 | Slave03 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9024 | Slave03 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9026 | Slave03 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9028 | Slave03 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9030 | Slave03 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9032 | Slave03 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9034 | Slave03 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9036 | Slave03 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9038 | Slave03 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9040 | Slave03 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9042 | Slave03 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9044 | Slave03 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9046 | Slave03 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9048 | Slave03 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9050 | Slave03 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9052 | Slave03 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9054 | Slave03 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9056 | Slave03 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9058 | Slave03 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9060 | Slave03 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9062 | Slave03 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9064 | Slave03 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9066 | Slave03 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9068 | Slave03 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9070 | Slave03 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9072 | Slave03 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9074 | Slave03 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9076 | Slave03 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9078 | Slave03 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9080 | Slave03 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9082 | Slave03 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9084 | Slave03 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9086 | Slave03 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9088 | Slave03 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9090 | Slave03 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9092 | Slave03 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9094 | Slave03 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9096 | Slave03 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9098 | Slave03 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9100 | Slave03 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9102 | Slave03 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9104 | Slave04 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9106 | Slave04 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9108 | Slave04 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9110 | Slave04 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9112 | Slave04 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9114 | Slave04 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9116 | Slave04 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9118 | Slave04 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9120 | Slave04 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9122 | Slave04 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9124 | Slave04 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9126 | Slave04 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9128 | Slave04 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9130 | Slave04 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9132 | Slave04 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9134 | Slave04 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9136 | Slave04 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9138 | Slave04 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9140 | Slave04 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9142 | Slave04 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9144 | Slave04 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9146 | Slave04 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9148 | Slave04 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9150 | Slave04 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9152 | Slave04 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9154 | Slave04 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9156 | Slave04 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9158 | Slave04 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9160 | Slave04 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9162 | Slave04 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9164 | Slave04 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9166 | Slave04 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9168 | Slave04 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9170 | Slave04 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9172 | Slave04 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9174 | Slave04 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9176 | Slave04 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9178 | Slave04 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9180 | Slave04 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9182 | Slave04 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9184 | Slave04 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9186 | Slave04 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9188 | Slave04 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9190 | Slave04 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9192 | Slave04 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9194 | Slave04 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9196 | Slave04 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9198 | Slave04 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9200 | Slave05 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9202 | Slave05 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9204 | Slave05 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9206 | Slave05 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9208 | Slave05 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9210 | Slave05 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9212 | Slave05 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9214 | Slave05 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9216 | Slave05 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9218 | Slave05 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9220 | Slave05 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9222 | Slave05 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9224 | Slave05 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9226 | Slave05 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9228 | Slave05 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9230 | Slave05 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9232 | Slave05 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9234 | Slave05 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9236 | Slave05 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9238 | Slave05 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9240 | Slave05 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9242 | Slave05 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9244 | Slave05 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9246 | Slave05 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9248 | Slave05 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9250 | Slave05 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9252 | Slave05 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9254 | Slave05 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9256 | Slave05 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9258 | Slave05 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9260 | Slave05 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9262 | Slave05 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9264 | Slave05 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9266 | Slave05 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9268 | Slave05 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9270 | Slave05 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9272 | Slave05 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9274 | Slave05 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9276 | Slave05 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9278 | Slave05 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9280 | Slave05 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9282 | Slave05 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9284 | Slave05 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9286 | Slave05 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9288 | Slave05 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9290 | Slave05 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9292 | Slave05 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9294 | Slave05 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9296 | Slave06 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9298 | Slave06 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9300 | Slave06 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9302 | Slave06 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9304 | Slave06 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9306 | Slave06 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9308 | Slave06 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9310 | Slave06 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9312 | Slave06 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9314 | Slave06 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9316 | Slave06 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9318 | Slave06 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9320 | Slave06 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9322 | Slave06 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9324 | Slave06 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9326 | Slave06 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9328 | Slave06 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9330 | Slave06 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9332 | Slave06 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9334 | Slave06 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9336 | Slave06 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9338 | Slave06 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9340 | Slave06 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9342 | Slave06 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9344 | Slave06 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9346 | Slave06 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9348 | Slave06 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9350 | Slave06 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9352 | Slave06 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9354 | Slave06 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9356 | Slave06 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9358 | Slave06 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9360 | Slave06 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9362 | Slave06 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9364 | Slave06 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9366 | Slave06 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9368 | Slave06 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9370 | Slave06 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9372 | Slave06 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9374 | Slave06 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9376 | Slave06 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9378 | Slave06 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9380 | Slave06 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9382 | Slave06 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9384 | Slave06 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9386 | Slave06 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9388 | Slave06 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9390 | Slave06 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9392 | Slave07 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9394 | Slave07 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9396 | Slave07 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9398 | Slave07 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9400 | Slave07 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9402 | Slave07 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9404 | Slave07 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9406 | Slave07 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9408 | Slave07 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9410 | Slave07 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9412 | Slave07 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9414 | Slave07 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9416 | Slave07 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9418 | Slave07 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9420 | Slave07 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9422 | Slave07 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9424 | Slave07 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9426 | Slave07 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9428 | Slave07 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9430 | Slave07 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9432 | Slave07 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9434 | Slave07 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9436 | Slave07 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9438 | Slave07 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9440 | Slave07 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9442 | Slave07 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9444 | Slave07 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9446 | Slave07 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9448 | Slave07 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9450 | Slave07 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9452 | Slave07 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9454 | Slave07 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9456 | Slave07 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9458 | Slave07 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9460 | Slave07 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9462 | Slave07 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9464 | Slave07 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9466 | Slave07 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9468 | Slave07 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9470 | Slave07 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9472 | Slave07 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9474 | Slave07 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9476 | Slave07 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9478 | Slave07 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9480 | Slave07 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9482 | Slave07 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9484 | Slave07 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9486 | Slave07 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9488 | Slave08 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9490 | Slave08 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9492 | Slave08 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9494 | Slave08 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9496 | Slave08 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9498 | Slave08 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9500 | Slave08 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9502 | Slave08 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9504 | Slave08 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9506 | Slave08 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9508 | Slave08 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9510 | Slave08 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9512 | Slave08 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9514 | Slave08 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9516 | Slave08 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9518 | Slave08 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9520 | Slave08 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9522 | Slave08 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9524 | Slave08 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9526 | Slave08 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9528 | Slave08 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9530 | Slave08 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9532 | Slave08 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9534 | Slave08 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9536 | Slave08 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9538 | Slave08 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9540 | Slave08 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9542 | Slave08 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9544 | Slave08 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9546 | Slave08 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9548 | Slave08 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9550 | Slave08 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9552 | Slave08 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9554 | Slave08 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9556 | Slave08 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9558 | Slave08 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9560 | Slave08 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9562 | Slave08 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9564 | Slave08 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9566 | Slave08 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9568 | Slave08 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9570 | Slave08 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9572 | Slave08 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9574 | Slave08 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9576 | Slave08 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9578 | Slave08 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9580 | Slave08 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9582 | Slave08 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9584 | Slave09 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9586 | Slave09 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9588 | Slave09 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9590 | Slave09 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9592 | Slave09 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9594 | Slave09 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9596 | Slave09 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9598 | Slave09 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9600 | Slave09 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9602 | Slave09 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9604 | Slave09 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9606 | Slave09 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9608 | Slave09 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9610 | Slave09 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9612 | Slave09 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9614 | Slave09 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9616 | Slave09 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9618 | Slave09 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9620 | Slave09 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9622 | Slave09 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9624 | Slave09 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9626 | Slave09 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9628 | Slave09 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9630 | Slave09 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9632 | Slave09 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9634 | Slave09 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9636 | Slave09 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9638 | Slave09 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9640 | Slave09 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9642 | Slave09 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9644 | Slave09 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9646 | Slave09 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9648 | Slave09 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9650 | Slave09 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9652 | Slave09 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9654 | Slave09 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9656 | Slave09 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9658 | Slave09 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9660 | Slave09 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9662 | Slave09 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9664 | Slave09 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9666 | Slave09 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9668 | Slave09 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9670 | Slave09 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9672 | Slave09 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9674 | Slave09 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9676 | Slave09 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9678 | Slave09 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9680 | Slave10 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9682 | Slave10 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9684 | Slave10 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9686 | Slave10 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9688 | Slave10 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9690 | Slave10 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9692 | Slave10 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9694 | Slave10 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9696 | Slave10 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9698 | Slave10 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9700 | Slave10 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9702 | Slave10 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9704 | Slave10 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9706 | Slave10 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9708 | Slave10 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9710 | Slave10 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9712 | Slave10 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9714 | Slave10 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9716 | Slave10 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9718 | Slave10 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9720 | Slave10 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9722 | Slave10 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9724 | Slave10 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9726 | Slave10 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9728 | Slave10 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9730 | Slave10 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9732 | Slave10 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9734 | Slave10 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9736 | Slave10 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9738 | Slave10 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9740 | Slave10 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9742 | Slave10 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9744 | Slave10 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9746 | Slave10 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9748 | Slave10 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9750 | Slave10 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9752 | Slave10 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9754 | Slave10 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9756 | Slave10 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9758 | Slave10 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9760 | Slave10 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9762 | Slave10 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9764 | Slave10 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9766 | Slave10 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9768 | Slave10 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9770 | Slave10 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9772 | Slave10 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9774 | Slave10 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9776 | Slave11 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9778 | Slave11 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9780 | Slave11 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9782 | Slave11 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9784 | Slave11 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9786 | Slave11 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9788 | Slave11 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9790 | Slave11 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9792 | Slave11 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9794 | Slave11 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9796 | Slave11 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9798 | Slave11 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9800 | Slave11 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9802 | Slave11 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9804 | Slave11 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9806 | Slave11 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9808 | Slave11 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9810 | Slave11 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9812 | Slave11 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9814 | Slave11 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9816 | Slave11 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9818 | Slave11 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9820 | Slave11 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9822 | Slave11 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9824 | Slave11 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9826 | Slave11 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9828 | Slave11 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9830 | Slave11 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9832 | Slave11 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9834 | Slave11 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9836 | Slave11 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9838 | Slave11 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9840 | Slave11 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9842 | Slave11 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9844 | Slave11 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9846 | Slave11 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9848 | Slave11 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9850 | Slave11 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9852 | Slave11 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9854 | Slave11 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9856 | Slave11 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9858 | Slave11 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9860 | Slave11 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9862 | Slave11 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9864 | Slave11 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9866 | Slave11 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9868 | Slave11 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9870 | Slave11 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9872 | Slave12 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9874 | Slave12 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9876 | Slave12 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9878 | Slave12 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9880 | Slave12 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9882 | Slave12 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9884 | Slave12 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9886 | Slave12 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9888 | Slave12 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9890 | Slave12 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9892 | Slave12 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9894 | Slave12 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9896 | Slave12 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9898 | Slave12 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9900 | Slave12 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9902 | Slave12 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
9904 | Slave12 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
9906 | Slave12 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
9908 | Slave12 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
9910 | Slave12 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
9912 | Slave12 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
9914 | Slave12 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
9916 | Slave12 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
9918 | Slave12 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
9920 | Slave12 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
9922 | Slave12 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
9924 | Slave12 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
9926 | Slave12 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
9928 | Slave12 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
9930 | Slave12 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
9932 | Slave12 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
9934 | Slave12 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
9936 | Slave12 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
9938 | Slave12 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
9940 | Slave12 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
9942 | Slave12 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
9944 | Slave12 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
9946 | Slave12 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
9948 | Slave12 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
9950 | Slave12 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
9952 | Slave12 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
9954 | Slave12 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
9956 | Slave12 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
9958 | Slave12 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
9960 | Slave12 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
9962 | Slave12 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
9964 | Slave12 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
9966 | Slave12 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
9968 | Slave13 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
9970 | Slave13 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
9972 | Slave13 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
9974 | Slave13 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
9976 | Slave13 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
9978 | Slave13 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
9980 | Slave13 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
9982 | Slave13 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
9984 | Slave13 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
9986 | Slave13 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
9988 | Slave13 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
9990 | Slave13 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
9992 | Slave13 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
9994 | Slave13 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
9996 | Slave13 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
9998 | Slave13 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
10000 | Slave13 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
10002 | Slave13 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
10004 | Slave13 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
10006 | Slave13 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
10008 | Slave13 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
10010 | Slave13 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
10012 | Slave13 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
10014 | Slave13 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
10016 | Slave13 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
10018 | Slave13 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
10020 | Slave13 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
10022 | Slave13 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
10024 | Slave13 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
10026 | Slave13 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
10028 | Slave13 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
10030 | Slave13 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
10032 | Slave13 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
10034 | Slave13 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
10036 | Slave13 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
10038 | Slave13 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
10040 | Slave13 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
10042 | Slave13 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
10044 | Slave13 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
10046 | Slave13 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
10048 | Slave13 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
10050 | Slave13 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
10052 | Slave13 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
10054 | Slave13 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
10056 | Slave13 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
10058 | Slave13 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
10060 | Slave13 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
10062 | Slave13 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
10064 | Slave14 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
10066 | Slave14 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
10068 | Slave14 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
10070 | Slave14 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
10072 | Slave14 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
10074 | Slave14 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
10076 | Slave14 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
10078 | Slave14 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
10080 | Slave14 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
10082 | Slave14 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
10084 | Slave14 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
10086 | Slave14 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
10088 | Slave14 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
10090 | Slave14 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
10092 | Slave14 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
10094 | Slave14 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
10096 | Slave14 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
10098 | Slave14 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
10100 | Slave14 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
10102 | Slave14 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
10104 | Slave14 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
10106 | Slave14 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
10108 | Slave14 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
10110 | Slave14 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
10112 | Slave14 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
10114 | Slave14 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
10116 | Slave14 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
10118 | Slave14 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
10120 | Slave14 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
10122 | Slave14 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
10124 | Slave14 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
10126 | Slave14 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
10128 | Slave14 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
10130 | Slave14 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
10132 | Slave14 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
10134 | Slave14 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
10136 | Slave14 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
10138 | Slave14 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
10140 | Slave14 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
10142 | Slave14 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
10144 | Slave14 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
10146 | Slave14 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
10148 | Slave14 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
10150 | Slave14 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
10152 | Slave14 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
10154 | Slave14 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
10156 | Slave14 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
10158 | Slave14 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
10160 | Slave15 Outlet Port01 Apparent Power | RO | 4 bytes | Unit:0.1
10162 | Slave15 Outlet Port02 Apparent Power | RO | 4 bytes | Unit:0.1
10164 | Slave15 Outlet Port03 Apparent Power | RO | 4 bytes | Unit:0.1
10166 | Slave15 Outlet Port04 Apparent Power | RO | 4 bytes | Unit:0.1
10168 | Slave15 Outlet Port05 Apparent Power | RO | 4 bytes | Unit:0.1
10170 | Slave15 Outlet Port06 Apparent Power | RO | 4 bytes | Unit:0.1
10172 | Slave15 Outlet Port07 Apparent Power | RO | 4 bytes | Unit:0.1
10174 | Slave15 Outlet Port08 Apparent Power | RO | 4 bytes | Unit:0.1
10176 | Slave15 Outlet Port09 Apparent Power | RO | 4 bytes | Unit:0.1
10178 | Slave15 Outlet Port10 Apparent Power | RO | 4 bytes | Unit:0.1
10180 | Slave15 Outlet Port11 Apparent Power | RO | 4 bytes | Unit:0.1
10182 | Slave15 Outlet Port12 Apparent Power | RO | 4 bytes | Unit:0.1
10184 | Slave15 Outlet Port13 Apparent Power | RO | 4 bytes | Unit:0.1
10186 | Slave15 Outlet Port14 Apparent Power | RO | 4 bytes | Unit:0.1
10188 | Slave15 Outlet Port15 Apparent Power | RO | 4 bytes | Unit:0.1
10190 | Slave15 Outlet Port16 Apparent Power | RO | 4 bytes | Unit:0.1
10192 | Slave15 Outlet Port17 Apparent Power | RO | 4 bytes | Unit:0.1
10194 | Slave15 Outlet Port18 Apparent Power | RO | 4 bytes | Unit:0.1
10196 | Slave15 Outlet Port19 Apparent Power | RO | 4 bytes | Unit:0.1
10198 | Slave15 Outlet Port20 Apparent Power | RO | 4 bytes | Unit:0.1
10200 | Slave15 Outlet Port21 Apparent Power | RO | 4 bytes | Unit:0.1
10202 | Slave15 Outlet Port22 Apparent Power | RO | 4 bytes | Unit:0.1
10204 | Slave15 Outlet Port23 Apparent Power | RO | 4 bytes | Unit:0.1
10206 | Slave15 Outlet Port24 Apparent Power | RO | 4 bytes | Unit:0.1
10208 | Slave15 Outlet Port25 Apparent Power | RO | 4 bytes | Unit:0.1
10210 | Slave15 Outlet Port26 Apparent Power | RO | 4 bytes | Unit:0.1
10212 | Slave15 Outlet Port27 Apparent Power | RO | 4 bytes | Unit:0.1
10214 | Slave15 Outlet Port28 Apparent Power | RO | 4 bytes | Unit:0.1
10216 | Slave15 Outlet Port29 Apparent Power | RO | 4 bytes | Unit:0.1
10218 | Slave15 Outlet Port30 Apparent Power | RO | 4 bytes | Unit:0.1
10220 | Slave15 Outlet Port31 Apparent Power | RO | 4 bytes | Unit:0.1
10222 | Slave15 Outlet Port32 Apparent Power | RO | 4 bytes | Unit:0.1
10224 | Slave15 Outlet Port33 Apparent Power | RO | 4 bytes | Unit:0.1
10226 | Slave15 Outlet Port34 Apparent Power | RO | 4 bytes | Unit:0.1
10228 | Slave15 Outlet Port35 Apparent Power | RO | 4 bytes | Unit:0.1
10230 | Slave15 Outlet Port36 Apparent Power | RO | 4 bytes | Unit:0.1
10232 | Slave15 Outlet Port37 Apparent Power | RO | 4 bytes | Unit:0.1
10234 | Slave15 Outlet Port38 Apparent Power | RO | 4 bytes | Unit:0.1
10236 | Slave15 Outlet Port39 Apparent Power | RO | 4 bytes | Unit:0.1
10238 | Slave15 Outlet Port40 Apparent Power | RO | 4 bytes | Unit:0.1
10240 | Slave15 Outlet Port41 Apparent Power | RO | 4 bytes | Unit:0.1
10242 | Slave15 Outlet Port42 Apparent Power | RO | 4 bytes | Unit:0.1
10244 | Slave15 Outlet Port43 Apparent Power | RO | 4 bytes | Unit:0.1
10246 | Slave15 Outlet Port44 Apparent Power | RO | 4 bytes | Unit:0.1
10248 | Slave15 Outlet Port45 Apparent Power | RO | 4 bytes | Unit:0.1
10250 | Slave15 Outlet Port46 Apparent Power | RO | 4 bytes | Unit:0.1
10252 | Slave15 Outlet Port47 Apparent Power | RO | 4 bytes | Unit:0.1
10254 | Slave15 Outlet Port48 Apparent Power | RO | 4 bytes | Unit:0.1
10256 | Master Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10258 | Master Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10260 | Master Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10262 | Master Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10264 | Master Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10266 | Master Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10268 | Master Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10270 | Master Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10272 | Master Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10274 | Master Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10276 | Master Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10278 | Master Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10280 | Master Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10282 | Master Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10284 | Master Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10286 | Master Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10288 | Master Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10290 | Master Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10292 | Master Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10294 | Master Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10296 | Master Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10298 | Master Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10300 | Master Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10302 | Master Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10304 | Master Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10306 | Master Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10308 | Master Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10310 | Master Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10312 | Master Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10314 | Master Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10316 | Master Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10318 | Master Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10320 | Master Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10322 | Master Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10324 | Master Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10326 | Master Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10328 | Master Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10330 | Master Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10332 | Master Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10334 | Master Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10336 | Master Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10338 | Master Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10340 | Master Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10342 | Master Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10344 | Master Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10346 | Master Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10348 | Master Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10350 | Master Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10352 | Slave01 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10354 | Slave01 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10356 | Slave01 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10358 | Slave01 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10360 | Slave01 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10362 | Slave01 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10364 | Slave01 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10366 | Slave01 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10368 | Slave01 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10370 | Slave01 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10372 | Slave01 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10374 | Slave01 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10376 | Slave01 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10378 | Slave01 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10380 | Slave01 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10382 | Slave01 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10384 | Slave01 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10386 | Slave01 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10388 | Slave01 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10390 | Slave01 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10392 | Slave01 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10394 | Slave01 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10396 | Slave01 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10398 | Slave01 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10400 | Slave01 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10402 | Slave01 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10404 | Slave01 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10406 | Slave01 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10408 | Slave01 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10410 | Slave01 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10412 | Slave01 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10414 | Slave01 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10416 | Slave01 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10418 | Slave01 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10420 | Slave01 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10422 | Slave01 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10424 | Slave01 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10426 | Slave01 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10428 | Slave01 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10430 | Slave01 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10432 | Slave01 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10434 | Slave01 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10436 | Slave01 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10438 | Slave01 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10440 | Slave01 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10442 | Slave01 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10444 | Slave01 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10446 | Slave01 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10448 | Slave02 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10450 | Slave02 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10452 | Slave02 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10454 | Slave02 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10456 | Slave02 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10458 | Slave02 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10460 | Slave02 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10462 | Slave02 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10464 | Slave02 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10466 | Slave02 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10468 | Slave02 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10470 | Slave02 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10472 | Slave02 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10474 | Slave02 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10476 | Slave02 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10478 | Slave02 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10480 | Slave02 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10482 | Slave02 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10484 | Slave02 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10486 | Slave02 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10488 | Slave02 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10490 | Slave02 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10492 | Slave02 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10494 | Slave02 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10496 | Slave02 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10498 | Slave02 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10500 | Slave02 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10502 | Slave02 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10504 | Slave02 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10506 | Slave02 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10508 | Slave02 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10510 | Slave02 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10512 | Slave02 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10514 | Slave02 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10516 | Slave02 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10518 | Slave02 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10520 | Slave02 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10522 | Slave02 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10524 | Slave02 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10526 | Slave02 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10528 | Slave02 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10530 | Slave02 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10532 | Slave02 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10534 | Slave02 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10536 | Slave02 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10538 | Slave02 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10540 | Slave02 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10542 | Slave02 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10544 | Slave03 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10546 | Slave03 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10548 | Slave03 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10550 | Slave03 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10552 | Slave03 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10554 | Slave03 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10556 | Slave03 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10558 | Slave03 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10560 | Slave03 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10562 | Slave03 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10564 | Slave03 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10566 | Slave03 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10568 | Slave03 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10570 | Slave03 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10572 | Slave03 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10574 | Slave03 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10576 | Slave03 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10578 | Slave03 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10580 | Slave03 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10582 | Slave03 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10584 | Slave03 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10586 | Slave03 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10588 | Slave03 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10590 | Slave03 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10592 | Slave03 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10594 | Slave03 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10596 | Slave03 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10598 | Slave03 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10600 | Slave03 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10602 | Slave03 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10604 | Slave03 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10606 | Slave03 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10608 | Slave03 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10610 | Slave03 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10612 | Slave03 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10614 | Slave03 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10616 | Slave03 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10618 | Slave03 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10620 | Slave03 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10622 | Slave03 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10624 | Slave03 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10626 | Slave03 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10628 | Slave03 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10630 | Slave03 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10632 | Slave03 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10634 | Slave03 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10636 | Slave03 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10638 | Slave03 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10640 | Slave04 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10642 | Slave04 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10644 | Slave04 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10646 | Slave04 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10648 | Slave04 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10650 | Slave04 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10652 | Slave04 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10654 | Slave04 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10656 | Slave04 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10658 | Slave04 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10660 | Slave04 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10662 | Slave04 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10664 | Slave04 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10666 | Slave04 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10668 | Slave04 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10670 | Slave04 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10672 | Slave04 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10674 | Slave04 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10676 | Slave04 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10678 | Slave04 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10680 | Slave04 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10682 | Slave04 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10684 | Slave04 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10686 | Slave04 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10688 | Slave04 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10690 | Slave04 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10692 | Slave04 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10694 | Slave04 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10696 | Slave04 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10698 | Slave04 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10700 | Slave04 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10702 | Slave04 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10704 | Slave04 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10706 | Slave04 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10708 | Slave04 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10710 | Slave04 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10712 | Slave04 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10714 | Slave04 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10716 | Slave04 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10718 | Slave04 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10720 | Slave04 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10722 | Slave04 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10724 | Slave04 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10726 | Slave04 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10728 | Slave04 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10730 | Slave04 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10732 | Slave04 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10734 | Slave04 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10736 | Slave05 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10738 | Slave05 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10740 | Slave05 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10742 | Slave05 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10744 | Slave05 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10746 | Slave05 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10748 | Slave05 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10750 | Slave05 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10752 | Slave05 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10754 | Slave05 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10756 | Slave05 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10758 | Slave05 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10760 | Slave05 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10762 | Slave05 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10764 | Slave05 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10766 | Slave05 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10768 | Slave05 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10770 | Slave05 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10772 | Slave05 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10774 | Slave05 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10776 | Slave05 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10778 | Slave05 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10780 | Slave05 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10782 | Slave05 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10784 | Slave05 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10786 | Slave05 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10788 | Slave05 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10790 | Slave05 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10792 | Slave05 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10794 | Slave05 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10796 | Slave05 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10798 | Slave05 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10800 | Slave05 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10802 | Slave05 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10804 | Slave05 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10806 | Slave05 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10808 | Slave05 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10810 | Slave05 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10812 | Slave05 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10814 | Slave05 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10816 | Slave05 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10818 | Slave05 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10820 | Slave05 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10822 | Slave05 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10824 | Slave05 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10826 | Slave05 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10828 | Slave05 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10830 | Slave05 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10832 | Slave06 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10834 | Slave06 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10836 | Slave06 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10838 | Slave06 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10840 | Slave06 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10842 | Slave06 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10844 | Slave06 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10846 | Slave06 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10848 | Slave06 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10850 | Slave06 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10852 | Slave06 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10854 | Slave06 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10856 | Slave06 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10858 | Slave06 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10860 | Slave06 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10862 | Slave06 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10864 | Slave06 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10866 | Slave06 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10868 | Slave06 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10870 | Slave06 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10872 | Slave06 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10874 | Slave06 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10876 | Slave06 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10878 | Slave06 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10880 | Slave06 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10882 | Slave06 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10884 | Slave06 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10886 | Slave06 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10888 | Slave06 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10890 | Slave06 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10892 | Slave06 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10894 | Slave06 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10896 | Slave06 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10898 | Slave06 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10900 | Slave06 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10902 | Slave06 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
10904 | Slave06 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
10906 | Slave06 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
10908 | Slave06 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
10910 | Slave06 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
10912 | Slave06 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
10914 | Slave06 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
10916 | Slave06 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
10918 | Slave06 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
10920 | Slave06 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
10922 | Slave06 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
10924 | Slave06 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
10926 | Slave06 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
10928 | Slave07 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
10930 | Slave07 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
10932 | Slave07 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
10934 | Slave07 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
10936 | Slave07 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
10938 | Slave07 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
10940 | Slave07 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
10942 | Slave07 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
10944 | Slave07 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
10946 | Slave07 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
10948 | Slave07 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
10950 | Slave07 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
10952 | Slave07 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
10954 | Slave07 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
10956 | Slave07 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
10958 | Slave07 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
10960 | Slave07 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
10962 | Slave07 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
10964 | Slave07 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
10966 | Slave07 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
10968 | Slave07 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
10970 | Slave07 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
10972 | Slave07 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
10974 | Slave07 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
10976 | Slave07 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
10978 | Slave07 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
10980 | Slave07 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
10982 | Slave07 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
10984 | Slave07 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
10986 | Slave07 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
10988 | Slave07 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
10990 | Slave07 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
10992 | Slave07 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
10994 | Slave07 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
10996 | Slave07 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
10998 | Slave07 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11000 | Slave07 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11002 | Slave07 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11004 | Slave07 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11006 | Slave07 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11008 | Slave07 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11010 | Slave07 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11012 | Slave07 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11014 | Slave07 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11016 | Slave07 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11018 | Slave07 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11020 | Slave07 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11022 | Slave07 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11024 | Slave08 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11026 | Slave08 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11028 | Slave08 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11030 | Slave08 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11032 | Slave08 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11034 | Slave08 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11036 | Slave08 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11038 | Slave08 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11040 | Slave08 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11042 | Slave08 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11044 | Slave08 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11046 | Slave08 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11048 | Slave08 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11050 | Slave08 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11052 | Slave08 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11054 | Slave08 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11056 | Slave08 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11058 | Slave08 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11060 | Slave08 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11062 | Slave08 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11064 | Slave08 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11066 | Slave08 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11068 | Slave08 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11070 | Slave08 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11072 | Slave08 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11074 | Slave08 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11076 | Slave08 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11078 | Slave08 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11080 | Slave08 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11082 | Slave08 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11084 | Slave08 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11086 | Slave08 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11088 | Slave08 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11090 | Slave08 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11092 | Slave08 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11094 | Slave08 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11096 | Slave08 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11098 | Slave08 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11100 | Slave08 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11102 | Slave08 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11104 | Slave08 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11106 | Slave08 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11108 | Slave08 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11110 | Slave08 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11112 | Slave08 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11114 | Slave08 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11116 | Slave08 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11118 | Slave08 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11120 | Slave09 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11122 | Slave09 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11124 | Slave09 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11126 | Slave09 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11128 | Slave09 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11130 | Slave09 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11132 | Slave09 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11134 | Slave09 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11136 | Slave09 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11138 | Slave09 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11140 | Slave09 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11142 | Slave09 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11144 | Slave09 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11146 | Slave09 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11148 | Slave09 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11150 | Slave09 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11152 | Slave09 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11154 | Slave09 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11156 | Slave09 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11158 | Slave09 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11160 | Slave09 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11162 | Slave09 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11164 | Slave09 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11166 | Slave09 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11168 | Slave09 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11170 | Slave09 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11172 | Slave09 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11174 | Slave09 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11176 | Slave09 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11178 | Slave09 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11180 | Slave09 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11182 | Slave09 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11184 | Slave09 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11186 | Slave09 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11188 | Slave09 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11190 | Slave09 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11192 | Slave09 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11194 | Slave09 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11196 | Slave09 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11198 | Slave09 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11200 | Slave09 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11202 | Slave09 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11204 | Slave09 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11206 | Slave09 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11208 | Slave09 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11210 | Slave09 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11212 | Slave09 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11214 | Slave09 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11216 | Slave10 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11218 | Slave10 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11220 | Slave10 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11222 | Slave10 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11224 | Slave10 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11226 | Slave10 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11228 | Slave10 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11230 | Slave10 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11232 | Slave10 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11234 | Slave10 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11236 | Slave10 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11238 | Slave10 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11240 | Slave10 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11242 | Slave10 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11244 | Slave10 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11246 | Slave10 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11248 | Slave10 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11250 | Slave10 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11252 | Slave10 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11254 | Slave10 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11256 | Slave10 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11258 | Slave10 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11260 | Slave10 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11262 | Slave10 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11264 | Slave10 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11266 | Slave10 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11268 | Slave10 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11270 | Slave10 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11272 | Slave10 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11274 | Slave10 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11276 | Slave10 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11278 | Slave10 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11280 | Slave10 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11282 | Slave10 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11284 | Slave10 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11286 | Slave10 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11288 | Slave10 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11290 | Slave10 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11292 | Slave10 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11294 | Slave10 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11296 | Slave10 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11298 | Slave10 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11300 | Slave10 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11302 | Slave10 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11304 | Slave10 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11306 | Slave10 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11308 | Slave10 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11310 | Slave10 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11312 | Slave11 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11314 | Slave11 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11316 | Slave11 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11318 | Slave11 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11320 | Slave11 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11322 | Slave11 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11324 | Slave11 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11326 | Slave11 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11328 | Slave11 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11330 | Slave11 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11332 | Slave11 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11334 | Slave11 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11336 | Slave11 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11338 | Slave11 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11340 | Slave11 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11342 | Slave11 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11344 | Slave11 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11346 | Slave11 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11348 | Slave11 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11350 | Slave11 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11352 | Slave11 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11354 | Slave11 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11356 | Slave11 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11358 | Slave11 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11360 | Slave11 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11362 | Slave11 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11364 | Slave11 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11366 | Slave11 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11368 | Slave11 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11370 | Slave11 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11372 | Slave11 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11374 | Slave11 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11376 | Slave11 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11378 | Slave11 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11380 | Slave11 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11382 | Slave11 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11384 | Slave11 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11386 | Slave11 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11388 | Slave11 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11390 | Slave11 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11392 | Slave11 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11394 | Slave11 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11396 | Slave11 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11398 | Slave11 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11400 | Slave11 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11402 | Slave11 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11404 | Slave11 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11406 | Slave11 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11408 | Slave12 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11410 | Slave12 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11412 | Slave12 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11414 | Slave12 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11416 | Slave12 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11418 | Slave12 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11420 | Slave12 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11422 | Slave12 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11424 | Slave12 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11426 | Slave12 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11428 | Slave12 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11430 | Slave12 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11432 | Slave12 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11434 | Slave12 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11436 | Slave12 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11438 | Slave12 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11440 | Slave12 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11442 | Slave12 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11444 | Slave12 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11446 | Slave12 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11448 | Slave12 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11450 | Slave12 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11452 | Slave12 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11454 | Slave12 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11456 | Slave12 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11458 | Slave12 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11460 | Slave12 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11462 | Slave12 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11464 | Slave12 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11466 | Slave12 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11468 | Slave12 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11470 | Slave12 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11472 | Slave12 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11474 | Slave12 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11476 | Slave12 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11478 | Slave12 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11480 | Slave12 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11482 | Slave12 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11484 | Slave12 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11486 | Slave12 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11488 | Slave12 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11490 | Slave12 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11492 | Slave12 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11494 | Slave12 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11496 | Slave12 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11498 | Slave12 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11500 | Slave12 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11502 | Slave12 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11504 | Slave13 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11506 | Slave13 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11508 | Slave13 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11510 | Slave13 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11512 | Slave13 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11514 | Slave13 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11516 | Slave13 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11518 | Slave13 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11520 | Slave13 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11522 | Slave13 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11524 | Slave13 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11526 | Slave13 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11528 | Slave13 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11530 | Slave13 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11532 | Slave13 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11534 | Slave13 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11536 | Slave13 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11538 | Slave13 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11540 | Slave13 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11542 | Slave13 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11544 | Slave13 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11546 | Slave13 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11548 | Slave13 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11550 | Slave13 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11552 | Slave13 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11554 | Slave13 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11556 | Slave13 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11558 | Slave13 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11560 | Slave13 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11562 | Slave13 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11564 | Slave13 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11566 | Slave13 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11568 | Slave13 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11570 | Slave13 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11572 | Slave13 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11574 | Slave13 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11576 | Slave13 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11578 | Slave13 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11580 | Slave13 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11582 | Slave13 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11584 | Slave13 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11586 | Slave13 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11588 | Slave13 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11590 | Slave13 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11592 | Slave13 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11594 | Slave13 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11596 | Slave13 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11598 | Slave13 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11600 | Slave14 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11602 | Slave14 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11604 | Slave14 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11606 | Slave14 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11608 | Slave14 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11610 | Slave14 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11612 | Slave14 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11614 | Slave14 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11616 | Slave14 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11618 | Slave14 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11620 | Slave14 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11622 | Slave14 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11624 | Slave14 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11626 | Slave14 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11628 | Slave14 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11630 | Slave14 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11632 | Slave14 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11634 | Slave14 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11636 | Slave14 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11638 | Slave14 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11640 | Slave14 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11642 | Slave14 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11644 | Slave14 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11646 | Slave14 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11648 | Slave14 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11650 | Slave14 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11652 | Slave14 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11654 | Slave14 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11656 | Slave14 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11658 | Slave14 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11660 | Slave14 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11662 | Slave14 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11664 | Slave14 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11666 | Slave14 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11668 | Slave14 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11670 | Slave14 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11672 | Slave14 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11674 | Slave14 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11676 | Slave14 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11678 | Slave14 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11680 | Slave14 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11682 | Slave14 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11684 | Slave14 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11686 | Slave14 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11688 | Slave14 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11690 | Slave14 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11692 | Slave14 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11694 | Slave14 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11696 | Slave15 Outlet Port01 Energy | RO | 4 bytes | Unit:0.001KW
11698 | Slave15 Outlet Port02 Energy | RO | 4 bytes | Unit:0.001KW
11700 | Slave15 Outlet Port03 Energy | RO | 4 bytes | Unit:0.001KW
11702 | Slave15 Outlet Port04 Energy | RO | 4 bytes | Unit:0.001KW
11704 | Slave15 Outlet Port05 Energy | RO | 4 bytes | Unit:0.001KW
11706 | Slave15 Outlet Port06 Energy | RO | 4 bytes | Unit:0.001KW
11708 | Slave15 Outlet Port07 Energy | RO | 4 bytes | Unit:0.001KW
11710 | Slave15 Outlet Port08 Energy | RO | 4 bytes | Unit:0.001KW
11712 | Slave15 Outlet Port09 Energy | RO | 4 bytes | Unit:0.001KW
11714 | Slave15 Outlet Port10 Energy | RO | 4 bytes | Unit:0.001KW
11716 | Slave15 Outlet Port11 Energy | RO | 4 bytes | Unit:0.001KW
11718 | Slave15 Outlet Port12 Energy | RO | 4 bytes | Unit:0.001KW
11720 | Slave15 Outlet Port13 Energy | RO | 4 bytes | Unit:0.001KW
11722 | Slave15 Outlet Port14 Energy | RO | 4 bytes | Unit:0.001KW
11724 | Slave15 Outlet Port15 Energy | RO | 4 bytes | Unit:0.001KW
11726 | Slave15 Outlet Port16 Energy | RO | 4 bytes | Unit:0.001KW
11728 | Slave15 Outlet Port17 Energy | RO | 4 bytes | Unit:0.001KW
11730 | Slave15 Outlet Port18 Energy | RO | 4 bytes | Unit:0.001KW
11732 | Slave15 Outlet Port19 Energy | RO | 4 bytes | Unit:0.001KW
11734 | Slave15 Outlet Port20 Energy | RO | 4 bytes | Unit:0.001KW
11736 | Slave15 Outlet Port21 Energy | RO | 4 bytes | Unit:0.001KW
11738 | Slave15 Outlet Port22 Energy | RO | 4 bytes | Unit:0.001KW
11740 | Slave15 Outlet Port23 Energy | RO | 4 bytes | Unit:0.001KW
11742 | Slave15 Outlet Port24 Energy | RO | 4 bytes | Unit:0.001KW
11744 | Slave15 Outlet Port25 Energy | RO | 4 bytes | Unit:0.001KW
11746 | Slave15 Outlet Port26 Energy | RO | 4 bytes | Unit:0.001KW
11748 | Slave15 Outlet Port27 Energy | RO | 4 bytes | Unit:0.001KW
11750 | Slave15 Outlet Port28 Energy | RO | 4 bytes | Unit:0.001KW
11752 | Slave15 Outlet Port29 Energy | RO | 4 bytes | Unit:0.001KW
11754 | Slave15 Outlet Port30 Energy | RO | 4 bytes | Unit:0.001KW
11756 | Slave15 Outlet Port31 Energy | RO | 4 bytes | Unit:0.001KW
11758 | Slave15 Outlet Port32 Energy | RO | 4 bytes | Unit:0.001KW
11760 | Slave15 Outlet Port33 Energy | RO | 4 bytes | Unit:0.001KW
11762 | Slave15 Outlet Port34 Energy | RO | 4 bytes | Unit:0.001KW
11764 | Slave15 Outlet Port35 Energy | RO | 4 bytes | Unit:0.001KW
11766 | Slave15 Outlet Port36 Energy | RO | 4 bytes | Unit:0.001KW
11768 | Slave15 Outlet Port37 Energy | RO | 4 bytes | Unit:0.001KW
11770 | Slave15 Outlet Port38 Energy | RO | 4 bytes | Unit:0.001KW
11772 | Slave15 Outlet Port39 Energy | RO | 4 bytes | Unit:0.001KW
11774 | Slave15 Outlet Port40 Energy | RO | 4 bytes | Unit:0.001KW
11776 | Slave15 Outlet Port41 Energy | RO | 4 bytes | Unit:0.001KW
11778 | Slave15 Outlet Port42 Energy | RO | 4 bytes | Unit:0.001KW
11780 | Slave15 Outlet Port43 Energy | RO | 4 bytes | Unit:0.001KW
11782 | Slave15 Outlet Port44 Energy | RO | 4 bytes | Unit:0.001KW
11784 | Slave15 Outlet Port45 Energy | RO | 4 bytes | Unit:0.001KW
11786 | Slave15 Outlet Port46 Energy | RO | 4 bytes | Unit:0.001KW
11788 | Slave15 Outlet Port47 Energy | RO | 4 bytes | Unit:0.001KW
11790 | Slave15 Outlet Port48 Energy | RO | 4 bytes | Unit:0.001KW
11792 | Master Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11793 | Slave01 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11794 | Slave02 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11795 | Slave03 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11796 | Slave04 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11797 | Slave05 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11798 | Slave06 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11799 | Slave07 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11800 | Slave08 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11801 | Slave09 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11802 | Slave10 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11803 | Slave11 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11804 | Slave12 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11805 | Slave13 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11806 | Slave14 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11807 | Slave15 Inlet Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
11808 | Master Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11809 | Slave01 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11810 | Slave02 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11811 | Slave03 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11812 | Slave04 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11813 | Slave05 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11814 | Slave06 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11815 | Slave07 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11816 | Slave08 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11817 | Slave09 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11818 | Slave10 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11819 | Slave11 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11820 | Slave12 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11821 | Slave13 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11822 | Slave14 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11823 | Slave15 Inlet Load Balance Warning | RW | 2 bytes | Unit:1%
11824 | Master Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11825 | Slave01 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11826 | Slave02 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11827 | Slave03 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11828 | Slave04 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11829 | Slave05 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11830 | Slave06 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11831 | Slave07 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11832 | Slave08 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11833 | Slave09 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11834 | Slave10 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11835 | Slave11 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11836 | Slave12 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11837 | Slave13 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11838 | Slave14 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11839 | Slave15 Inlet Load Balance Critical | RW | 2 bytes | Unit:1%
11840 | Master Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11841 | Slave01 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11842 | Slave02 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11843 | Slave03 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11844 | Slave04 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11845 | Slave05 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11846 | Slave06 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11847 | Slave07 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11848 | Slave08 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11849 | Slave09 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11850 | Slave10 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11851 | Slave11 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11852 | Slave12 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11853 | Slave13 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11854 | Slave14 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11855 | Slave15 Inlet Phase1 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11856 | Master Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11857 | Slave01 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11858 | Slave02 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11859 | Slave03 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11860 | Slave04 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11861 | Slave05 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11862 | Slave06 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11863 | Slave07 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11864 | Slave08 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11865 | Slave09 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11866 | Slave10 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11867 | Slave11 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11868 | Slave12 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11869 | Slave13 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11870 | Slave14 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11871 | Slave15 Inlet Phase2 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11872 | Master Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11873 | Slave01 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11874 | Slave02 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11875 | Slave03 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11876 | Slave04 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11877 | Slave05 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11878 | Slave06 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11879 | Slave07 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11880 | Slave08 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11881 | Slave09 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11882 | Slave10 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11883 | Slave11 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11884 | Slave12 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11885 | Slave13 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11886 | Slave14 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11887 | Slave15 Inlet Phase3 Over Voltage Warning | RW | 2 bytes | Unit:0.1
11888 | Master Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11889 | Slave01 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11890 | Slave02 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11891 | Slave03 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11892 | Slave04 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11893 | Slave05 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11894 | Slave06 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11895 | Slave07 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11896 | Slave08 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11897 | Slave09 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11898 | Slave10 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11899 | Slave11 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11900 | Slave12 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11901 | Slave13 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11902 | Slave14 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11903 | Slave15 Inlet Phase1 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11904 | Master Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11905 | Slave01 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11906 | Slave02 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11907 | Slave03 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11908 | Slave04 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11909 | Slave05 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11910 | Slave06 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11911 | Slave07 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11912 | Slave08 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11913 | Slave09 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11914 | Slave10 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11915 | Slave11 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11916 | Slave12 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11917 | Slave13 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11918 | Slave14 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11919 | Slave15 Inlet Phase2 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11920 | Master Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11921 | Slave01 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11922 | Slave02 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11923 | Slave03 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11924 | Slave04 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11925 | Slave05 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11926 | Slave06 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11927 | Slave07 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11928 | Slave08 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11929 | Slave09 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11930 | Slave10 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11931 | Slave11 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11932 | Slave12 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11933 | Slave13 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11934 | Slave14 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11935 | Slave15 Inlet Phase3 Over Voltage Critical | RW | 2 bytes | Unit:0.1
11936 | Master Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11937 | Slave01 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11938 | Slave02 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11939 | Slave03 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11940 | Slave04 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11941 | Slave05 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11942 | Slave06 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11943 | Slave07 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11944 | Slave08 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11945 | Slave09 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11946 | Slave10 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11947 | Slave11 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11948 | Slave12 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11949 | Slave13 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11950 | Slave14 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11951 | Slave15 Inlet Phase1 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11952 | Master Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11953 | Slave01 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11954 | Slave02 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11955 | Slave03 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11956 | Slave04 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11957 | Slave05 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11958 | Slave06 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11959 | Slave07 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11960 | Slave08 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11961 | Slave09 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11962 | Slave10 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11963 | Slave11 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11964 | Slave12 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11965 | Slave13 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11966 | Slave14 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11967 | Slave15 Inlet Phase2 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11968 | Master Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11969 | Slave01 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11970 | Slave02 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11971 | Slave03 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11972 | Slave04 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11973 | Slave05 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11974 | Slave06 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11975 | Slave07 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11976 | Slave08 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11977 | Slave09 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11978 | Slave10 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11979 | Slave11 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11980 | Slave12 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11981 | Slave13 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11982 | Slave14 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11983 | Slave15 Inlet Phase3 Total Over Current Warning | RW | 2 bytes | Unit:0.01
11984 | Master Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11985 | Slave01 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11986 | Slave02 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11987 | Slave03 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11988 | Slave04 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11989 | Slave05 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11990 | Slave06 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11991 | Slave07 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11992 | Slave08 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11993 | Slave09 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11994 | Slave10 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11995 | Slave11 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11996 | Slave12 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11997 | Slave13 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11998 | Slave14 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
11999 | Slave15 Inlet Phase1 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12000 | Master Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12001 | Slave01 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12002 | Slave02 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12003 | Slave03 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12004 | Slave04 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12005 | Slave05 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12006 | Slave06 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12007 | Slave07 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12008 | Slave08 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12009 | Slave09 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12010 | Slave10 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12011 | Slave11 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12012 | Slave12 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12013 | Slave13 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12014 | Slave14 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12015 | Slave15 Inlet Phase2 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12016 | Master Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12017 | Slave01 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12018 | Slave02 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12019 | Slave03 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12020 | Slave04 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12021 | Slave05 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12022 | Slave06 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12023 | Slave07 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12024 | Slave08 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12025 | Slave09 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12026 | Slave10 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12027 | Slave11 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12028 | Slave12 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12029 | Slave13 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12030 | Slave14 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12031 | Slave15 Inlet Phase3 Total Over Current Critical | RW | 2 bytes | Unit:0.01
12032 | Master Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12033 | Slave01 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12034 | Slave02 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12035 | Slave03 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12036 | Slave04 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12037 | Slave05 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12038 | Slave06 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12039 | Slave07 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12040 | Slave08 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12041 | Slave09 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12042 | Slave10 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12043 | Slave11 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12044 | Slave12 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12045 | Slave13 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12046 | Slave14 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12047 | Slave15 Inlet Phase1 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12048 | Master Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12049 | Slave01 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12050 | Slave02 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12051 | Slave03 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12052 | Slave04 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12053 | Slave05 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12054 | Slave06 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12055 | Slave07 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12056 | Slave08 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12057 | Slave09 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12058 | Slave10 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12059 | Slave11 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12060 | Slave12 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12061 | Slave13 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12062 | Slave14 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12063 | Slave15 Inlet Phase2 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12064 | Master Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12065 | Slave01 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12066 | Slave02 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12067 | Slave03 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12068 | Slave04 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12069 | Slave05 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12070 | Slave06 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12071 | Slave07 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12072 | Slave08 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12073 | Slave09 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12074 | Slave10 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12075 | Slave11 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12076 | Slave12 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12077 | Slave13 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12078 | Slave14 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12079 | Slave15 Inlet Phase3 Branch1 Over Current Warning | RW | 2 bytes | Unit:0.01
12080 | Master Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12081 | Slave01 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12082 | Slave02 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12083 | Slave03 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12084 | Slave04 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12085 | Slave05 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12086 | Slave06 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12087 | Slave07 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12088 | Slave08 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12089 | Slave09 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12090 | Slave10 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12091 | Slave11 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12092 | Slave12 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12093 | Slave13 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12094 | Slave14 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12095 | Slave15 Inlet Phase1 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12096 | Master Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12097 | Slave01 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12098 | Slave02 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12099 | Slave03 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12100 | Slave04 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12101 | Slave05 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12102 | Slave06 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12103 | Slave07 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12104 | Slave08 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12105 | Slave09 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12106 | Slave10 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12107 | Slave11 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12108 | Slave12 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12109 | Slave13 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12110 | Slave14 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12111 | Slave15 Inlet Phase2 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12112 | Master Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12113 | Slave01 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12114 | Slave02 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12115 | Slave03 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12116 | Slave04 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12117 | Slave05 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12118 | Slave06 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12119 | Slave07 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12120 | Slave08 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12121 | Slave09 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12122 | Slave10 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12123 | Slave11 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12124 | Slave12 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12125 | Slave13 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12126 | Slave14 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12127 | Slave15 Inlet Phase3 Branch1 Over Current Critical | RW | 2 bytes | Unit:0.01
12128 | Master Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12129 | Slave01 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12130 | Slave02 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12131 | Slave03 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12132 | Slave04 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12133 | Slave05 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12134 | Slave06 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12135 | Slave07 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12136 | Slave08 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12137 | Slave09 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12138 | Slave10 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12139 | Slave11 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12140 | Slave12 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12141 | Slave13 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12142 | Slave14 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12143 | Slave15 Inlet Phase1 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12144 | Master Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12145 | Slave01 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12146 | Slave02 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12147 | Slave03 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12148 | Slave04 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12149 | Slave05 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12150 | Slave06 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12151 | Slave07 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12152 | Slave08 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12153 | Slave09 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12154 | Slave10 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12155 | Slave11 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12156 | Slave12 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12157 | Slave13 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12158 | Slave14 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12159 | Slave15 Inlet Phase2 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12160 | Master Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12161 | Slave01 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12162 | Slave02 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12163 | Slave03 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12164 | Slave04 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12165 | Slave05 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12166 | Slave06 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12167 | Slave07 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12168 | Slave08 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12169 | Slave09 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12170 | Slave10 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12171 | Slave11 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12172 | Slave12 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12173 | Slave13 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12174 | Slave14 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12175 | Slave15 Inlet Phase3 Branch2 Over Current Warning | RW | 2 bytes | Unit:0.01
12176 | Master Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12177 | Slave01 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12178 | Slave02 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12179 | Slave03 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12180 | Slave04 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12181 | Slave05 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12182 | Slave06 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12183 | Slave07 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12184 | Slave08 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12185 | Slave09 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12186 | Slave10 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12187 | Slave11 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12188 | Slave12 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12189 | Slave13 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12190 | Slave14 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12191 | Slave15 Inlet Phase1 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12192 | Master Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12193 | Slave01 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12194 | Slave02 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12195 | Slave03 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12196 | Slave04 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12197 | Slave05 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12198 | Slave06 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12199 | Slave07 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12200 | Slave08 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12201 | Slave09 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12202 | Slave10 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12203 | Slave11 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12204 | Slave12 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12205 | Slave13 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12206 | Slave14 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12207 | Slave15 Inlet Phase2 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12208 | Master Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12209 | Slave01 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12210 | Slave02 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12211 | Slave03 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12212 | Slave04 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12213 | Slave05 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12214 | Slave06 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12215 | Slave07 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12216 | Slave08 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12217 | Slave09 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12218 | Slave10 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12219 | Slave11 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12220 | Slave12 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12221 | Slave13 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12222 | Slave14 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12223 | Slave15 Inlet Phase3 Branch2 Over Current Critical | RW | 2 bytes | Unit:0.01
12224 | Master Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12225 | Slave01 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12226 | Slave02 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12227 | Slave03 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12228 | Slave04 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12229 | Slave05 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12230 | Slave06 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12231 | Slave07 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12232 | Slave08 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12233 | Slave09 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12234 | Slave10 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12235 | Slave11 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12236 | Slave12 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12237 | Slave13 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12238 | Slave14 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12239 | Slave15 Inlet Leakage Current Threshold | RW | 2 bytes | Unit:1mA
12240 | Master Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12241 | Slave01 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12242 | Slave02 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12243 | Slave03 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12244 | Slave04 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12245 | Slave05 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12246 | Slave06 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12247 | Slave07 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12248 | Slave08 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12249 | Slave09 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12250 | Slave10 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12251 | Slave11 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12252 | Slave12 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12253 | Slave13 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12254 | Slave14 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12255 | Slave15 Inlet Phase1 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12256 | Master Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12257 | Slave01 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12258 | Slave02 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12259 | Slave03 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12260 | Slave04 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12261 | Slave05 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12262 | Slave06 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12263 | Slave07 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12264 | Slave08 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12265 | Slave09 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12266 | Slave10 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12267 | Slave11 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12268 | Slave12 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12269 | Slave13 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12270 | Slave14 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12271 | Slave15 Inlet Phase2 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12272 | Master Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12273 | Slave01 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12274 | Slave02 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12275 | Slave03 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12276 | Slave04 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12277 | Slave05 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12278 | Slave06 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12279 | Slave07 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12280 | Slave08 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12281 | Slave09 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12282 | Slave10 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12283 | Slave11 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12284 | Slave12 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12285 | Slave13 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12286 | Slave14 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12287 | Slave15 Inlet Phase3 Branch1 Over PF Warning | RW | 2 bytes | Unit:0.01
12288 | Master Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12289 | Slave01 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12290 | Slave02 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12291 | Slave03 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12292 | Slave04 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12293 | Slave05 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12294 | Slave06 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12295 | Slave07 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12296 | Slave08 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12297 | Slave09 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12298 | Slave10 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12299 | Slave11 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12300 | Slave12 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12301 | Slave13 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12302 | Slave14 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12303 | Slave15 Inlet Phase1 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12304 | Master Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12305 | Slave01 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12306 | Slave02 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12307 | Slave03 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12308 | Slave04 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12309 | Slave05 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12310 | Slave06 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12311 | Slave07 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12312 | Slave08 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12313 | Slave09 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12314 | Slave10 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12315 | Slave11 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12316 | Slave12 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12317 | Slave13 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12318 | Slave14 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12319 | Slave15 Inlet Phase2 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12320 | Master Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12321 | Slave01 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12322 | Slave02 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12323 | Slave03 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12324 | Slave04 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12325 | Slave05 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12326 | Slave06 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12327 | Slave07 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12328 | Slave08 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12329 | Slave09 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12330 | Slave10 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12331 | Slave11 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12332 | Slave12 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12333 | Slave13 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12334 | Slave14 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12335 | Slave15 Inlet Phase3 Branch1 Over PF Critical | RW | 2 bytes | Unit:0.01
12336 | Master Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12337 | Slave01 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12338 | Slave02 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12339 | Slave03 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12340 | Slave04 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12341 | Slave05 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12342 | Slave06 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12343 | Slave07 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12344 | Slave08 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12345 | Slave09 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12346 | Slave10 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12347 | Slave11 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12348 | Slave12 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12349 | Slave13 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12350 | Slave14 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12351 | Slave15 Inlet Phase1 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12352 | Master Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12353 | Slave01 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12354 | Slave02 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12355 | Slave03 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12356 | Slave04 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12357 | Slave05 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12358 | Slave06 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12359 | Slave07 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12360 | Slave08 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12361 | Slave09 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12362 | Slave10 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12363 | Slave11 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12364 | Slave12 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12365 | Slave13 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12366 | Slave14 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12367 | Slave15 Inlet Phase2 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12368 | Master Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12369 | Slave01 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12370 | Slave02 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12371 | Slave03 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12372 | Slave04 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12373 | Slave05 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12374 | Slave06 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12375 | Slave07 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12376 | Slave08 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12377 | Slave09 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12378 | Slave10 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12379 | Slave11 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12380 | Slave12 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12381 | Slave13 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12382 | Slave14 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12383 | Slave15 Inlet Phase3 Branch2 Over PF Warning | RW | 2 bytes | Unit:0.01
12384 | Master Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12385 | Slave01 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12386 | Slave02 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12387 | Slave03 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12388 | Slave04 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12389 | Slave05 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12390 | Slave06 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12391 | Slave07 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12392 | Slave08 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12393 | Slave09 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12394 | Slave10 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12395 | Slave11 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12396 | Slave12 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12397 | Slave13 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12398 | Slave14 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12399 | Slave15 Inlet Phase1 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12400 | Master Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12401 | Slave01 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12402 | Slave02 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12403 | Slave03 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12404 | Slave04 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12405 | Slave05 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12406 | Slave06 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12407 | Slave07 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12408 | Slave08 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12409 | Slave09 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12410 | Slave10 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12411 | Slave11 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12412 | Slave12 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12413 | Slave13 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12414 | Slave14 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12415 | Slave15 Inlet Phase2 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12416 | Master Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12417 | Slave01 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12418 | Slave02 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12419 | Slave03 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12420 | Slave04 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12421 | Slave05 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12422 | Slave06 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12423 | Slave07 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12424 | Slave08 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12425 | Slave09 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12426 | Slave10 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12427 | Slave11 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12428 | Slave12 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12429 | Slave13 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12430 | Slave14 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12431 | Slave15 Inlet Phase3 Branch2 Over PF Critical | RW | 2 bytes | Unit:0.01
12432 | Master Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12433 | Slave01 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12434 | Slave02 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12435 | Slave03 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12436 | Slave04 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12437 | Slave05 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12438 | Slave06 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12439 | Slave07 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12440 | Slave08 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12441 | Slave09 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12442 | Slave10 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12443 | Slave11 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12444 | Slave12 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12445 | Slave13 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12446 | Slave14 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12447 | Slave15 Inlet Sequential Startup Configuration | RW | 2 bytes | 0:All outlets which were ON before Power OFF should be switching ON with a time delay; 1:All outlets should stay OFF
12448 | Master Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12449 | Master Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12450 | Master Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12451 | Master Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12452 | Master Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12453 | Master Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12454 | Master Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12455 | Master Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12456 | Master Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12457 | Master Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12458 | Master Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12459 | Master Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12460 | Master Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12461 | Master Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12462 | Master Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12463 | Master Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12464 | Master Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12465 | Master Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12466 | Master Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12467 | Master Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12468 | Master Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12469 | Master Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12470 | Master Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12471 | Master Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12472 | Master Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12473 | Master Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12474 | Master Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12475 | Master Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12476 | Master Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12477 | Master Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12478 | Master Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12479 | Master Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12480 | Master Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12481 | Master Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12482 | Master Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12483 | Master Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12484 | Master Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12485 | Master Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12486 | Master Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12487 | Master Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12488 | Master Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12489 | Master Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12490 | Master Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12491 | Master Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12492 | Master Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12493 | Master Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12494 | Master Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12495 | Master Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12496 | Slave01 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12497 | Slave01 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12498 | Slave01 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12499 | Slave01 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12500 | Slave01 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12501 | Slave01 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12502 | Slave01 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12503 | Slave01 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12504 | Slave01 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12505 | Slave01 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12506 | Slave01 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12507 | Slave01 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12508 | Slave01 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12509 | Slave01 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12510 | Slave01 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12511 | Slave01 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12512 | Slave01 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12513 | Slave01 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12514 | Slave01 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12515 | Slave01 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12516 | Slave01 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12517 | Slave01 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12518 | Slave01 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12519 | Slave01 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12520 | Slave01 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12521 | Slave01 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12522 | Slave01 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12523 | Slave01 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12524 | Slave01 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12525 | Slave01 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12526 | Slave01 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12527 | Slave01 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12528 | Slave01 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12529 | Slave01 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12530 | Slave01 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12531 | Slave01 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12532 | Slave01 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12533 | Slave01 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12534 | Slave01 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12535 | Slave01 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12536 | Slave01 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12537 | Slave01 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12538 | Slave01 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12539 | Slave01 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12540 | Slave01 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12541 | Slave01 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12542 | Slave01 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12543 | Slave01 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12544 | Slave02 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12545 | Slave02 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12546 | Slave02 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12547 | Slave02 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12548 | Slave02 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12549 | Slave02 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12550 | Slave02 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12551 | Slave02 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12552 | Slave02 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12553 | Slave02 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12554 | Slave02 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12555 | Slave02 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12556 | Slave02 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12557 | Slave02 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12558 | Slave02 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12559 | Slave02 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12560 | Slave02 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12561 | Slave02 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12562 | Slave02 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12563 | Slave02 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12564 | Slave02 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12565 | Slave02 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12566 | Slave02 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12567 | Slave02 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12568 | Slave02 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12569 | Slave02 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12570 | Slave02 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12571 | Slave02 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12572 | Slave02 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12573 | Slave02 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12574 | Slave02 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12575 | Slave02 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12576 | Slave02 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12577 | Slave02 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12578 | Slave02 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12579 | Slave02 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12580 | Slave02 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12581 | Slave02 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12582 | Slave02 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12583 | Slave02 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12584 | Slave02 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12585 | Slave02 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12586 | Slave02 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12587 | Slave02 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12588 | Slave02 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12589 | Slave02 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12590 | Slave02 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12591 | Slave02 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12592 | Slave03 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12593 | Slave03 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12594 | Slave03 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12595 | Slave03 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12596 | Slave03 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12597 | Slave03 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12598 | Slave03 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12599 | Slave03 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12600 | Slave03 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12601 | Slave03 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12602 | Slave03 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12603 | Slave03 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12604 | Slave03 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12605 | Slave03 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12606 | Slave03 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12607 | Slave03 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12608 | Slave03 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12609 | Slave03 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12610 | Slave03 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12611 | Slave03 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12612 | Slave03 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12613 | Slave03 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12614 | Slave03 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12615 | Slave03 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12616 | Slave03 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12617 | Slave03 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12618 | Slave03 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12619 | Slave03 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12620 | Slave03 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12621 | Slave03 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12622 | Slave03 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12623 | Slave03 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12624 | Slave03 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12625 | Slave03 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12626 | Slave03 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12627 | Slave03 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12628 | Slave03 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12629 | Slave03 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12630 | Slave03 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12631 | Slave03 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12632 | Slave03 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12633 | Slave03 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12634 | Slave03 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12635 | Slave03 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12636 | Slave03 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12637 | Slave03 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12638 | Slave03 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12639 | Slave03 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12640 | Slave04 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12641 | Slave04 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12642 | Slave04 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12643 | Slave04 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12644 | Slave04 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12645 | Slave04 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12646 | Slave04 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12647 | Slave04 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12648 | Slave04 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12649 | Slave04 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12650 | Slave04 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12651 | Slave04 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12652 | Slave04 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12653 | Slave04 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12654 | Slave04 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12655 | Slave04 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12656 | Slave04 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12657 | Slave04 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12658 | Slave04 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12659 | Slave04 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12660 | Slave04 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12661 | Slave04 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12662 | Slave04 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12663 | Slave04 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12664 | Slave04 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12665 | Slave04 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12666 | Slave04 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12667 | Slave04 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12668 | Slave04 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12669 | Slave04 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12670 | Slave04 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12671 | Slave04 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12672 | Slave04 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12673 | Slave04 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12674 | Slave04 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12675 | Slave04 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12676 | Slave04 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12677 | Slave04 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12678 | Slave04 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12679 | Slave04 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12680 | Slave04 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12681 | Slave04 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12682 | Slave04 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12683 | Slave04 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12684 | Slave04 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12685 | Slave04 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12686 | Slave04 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12687 | Slave04 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12688 | Slave05 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12689 | Slave05 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12690 | Slave05 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12691 | Slave05 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12692 | Slave05 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12693 | Slave05 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12694 | Slave05 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12695 | Slave05 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12696 | Slave05 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12697 | Slave05 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12698 | Slave05 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12699 | Slave05 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12700 | Slave05 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12701 | Slave05 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12702 | Slave05 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12703 | Slave05 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12704 | Slave05 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12705 | Slave05 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12706 | Slave05 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12707 | Slave05 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12708 | Slave05 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12709 | Slave05 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12710 | Slave05 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12711 | Slave05 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12712 | Slave05 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12713 | Slave05 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12714 | Slave05 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12715 | Slave05 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12716 | Slave05 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12717 | Slave05 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12718 | Slave05 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12719 | Slave05 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12720 | Slave05 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12721 | Slave05 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12722 | Slave05 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12723 | Slave05 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12724 | Slave05 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12725 | Slave05 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12726 | Slave05 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12727 | Slave05 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12728 | Slave05 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12729 | Slave05 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12730 | Slave05 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12731 | Slave05 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12732 | Slave05 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12733 | Slave05 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12734 | Slave05 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12735 | Slave05 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12736 | Slave06 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12737 | Slave06 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12738 | Slave06 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12739 | Slave06 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12740 | Slave06 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12741 | Slave06 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12742 | Slave06 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12743 | Slave06 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12744 | Slave06 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12745 | Slave06 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12746 | Slave06 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12747 | Slave06 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12748 | Slave06 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12749 | Slave06 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12750 | Slave06 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12751 | Slave06 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12752 | Slave06 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12753 | Slave06 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12754 | Slave06 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12755 | Slave06 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12756 | Slave06 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12757 | Slave06 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12758 | Slave06 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12759 | Slave06 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12760 | Slave06 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12761 | Slave06 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12762 | Slave06 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12763 | Slave06 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12764 | Slave06 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12765 | Slave06 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12766 | Slave06 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12767 | Slave06 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12768 | Slave06 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12769 | Slave06 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12770 | Slave06 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12771 | Slave06 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12772 | Slave06 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12773 | Slave06 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12774 | Slave06 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12775 | Slave06 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12776 | Slave06 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12777 | Slave06 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12778 | Slave06 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12779 | Slave06 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12780 | Slave06 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12781 | Slave06 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12782 | Slave06 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12783 | Slave06 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12784 | Slave07 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12785 | Slave07 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12786 | Slave07 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12787 | Slave07 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12788 | Slave07 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12789 | Slave07 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12790 | Slave07 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12791 | Slave07 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12792 | Slave07 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12793 | Slave07 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12794 | Slave07 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12795 | Slave07 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12796 | Slave07 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12797 | Slave07 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12798 | Slave07 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12799 | Slave07 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12800 | Slave07 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12801 | Slave07 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12802 | Slave07 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12803 | Slave07 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12804 | Slave07 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12805 | Slave07 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12806 | Slave07 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12807 | Slave07 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12808 | Slave07 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12809 | Slave07 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12810 | Slave07 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12811 | Slave07 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12812 | Slave07 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12813 | Slave07 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12814 | Slave07 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12815 | Slave07 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12816 | Slave07 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12817 | Slave07 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12818 | Slave07 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12819 | Slave07 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12820 | Slave07 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12821 | Slave07 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12822 | Slave07 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12823 | Slave07 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12824 | Slave07 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12825 | Slave07 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12826 | Slave07 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12827 | Slave07 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12828 | Slave07 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12829 | Slave07 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12830 | Slave07 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12831 | Slave07 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12832 | Slave08 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12833 | Slave08 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12834 | Slave08 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12835 | Slave08 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12836 | Slave08 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12837 | Slave08 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12838 | Slave08 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12839 | Slave08 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12840 | Slave08 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12841 | Slave08 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12842 | Slave08 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12843 | Slave08 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12844 | Slave08 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12845 | Slave08 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12846 | Slave08 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12847 | Slave08 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12848 | Slave08 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12849 | Slave08 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12850 | Slave08 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12851 | Slave08 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12852 | Slave08 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12853 | Slave08 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12854 | Slave08 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12855 | Slave08 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12856 | Slave08 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12857 | Slave08 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12858 | Slave08 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12859 | Slave08 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12860 | Slave08 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12861 | Slave08 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12862 | Slave08 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12863 | Slave08 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12864 | Slave08 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12865 | Slave08 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12866 | Slave08 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12867 | Slave08 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12868 | Slave08 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12869 | Slave08 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12870 | Slave08 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12871 | Slave08 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12872 | Slave08 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12873 | Slave08 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12874 | Slave08 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12875 | Slave08 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12876 | Slave08 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12877 | Slave08 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12878 | Slave08 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12879 | Slave08 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12880 | Slave09 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12881 | Slave09 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12882 | Slave09 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12883 | Slave09 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12884 | Slave09 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12885 | Slave09 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12886 | Slave09 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12887 | Slave09 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12888 | Slave09 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12889 | Slave09 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12890 | Slave09 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12891 | Slave09 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12892 | Slave09 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12893 | Slave09 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12894 | Slave09 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12895 | Slave09 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12896 | Slave09 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12897 | Slave09 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12898 | Slave09 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12899 | Slave09 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12900 | Slave09 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12901 | Slave09 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12902 | Slave09 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12903 | Slave09 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12904 | Slave09 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12905 | Slave09 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12906 | Slave09 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12907 | Slave09 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12908 | Slave09 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12909 | Slave09 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12910 | Slave09 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12911 | Slave09 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12912 | Slave09 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12913 | Slave09 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12914 | Slave09 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12915 | Slave09 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12916 | Slave09 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12917 | Slave09 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12918 | Slave09 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12919 | Slave09 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12920 | Slave09 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12921 | Slave09 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12922 | Slave09 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12923 | Slave09 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12924 | Slave09 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12925 | Slave09 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12926 | Slave09 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12927 | Slave09 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12928 | Slave10 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12929 | Slave10 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12930 | Slave10 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12931 | Slave10 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12932 | Slave10 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12933 | Slave10 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12934 | Slave10 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12935 | Slave10 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12936 | Slave10 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12937 | Slave10 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12938 | Slave10 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12939 | Slave10 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12940 | Slave10 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12941 | Slave10 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12942 | Slave10 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12943 | Slave10 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12944 | Slave10 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12945 | Slave10 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12946 | Slave10 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12947 | Slave10 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12948 | Slave10 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12949 | Slave10 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12950 | Slave10 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12951 | Slave10 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12952 | Slave10 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12953 | Slave10 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12954 | Slave10 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12955 | Slave10 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12956 | Slave10 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12957 | Slave10 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12958 | Slave10 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12959 | Slave10 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12960 | Slave10 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12961 | Slave10 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12962 | Slave10 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12963 | Slave10 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12964 | Slave10 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12965 | Slave10 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12966 | Slave10 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12967 | Slave10 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12968 | Slave10 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12969 | Slave10 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12970 | Slave10 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12971 | Slave10 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12972 | Slave10 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12973 | Slave10 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12974 | Slave10 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12975 | Slave10 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12976 | Slave11 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12977 | Slave11 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12978 | Slave11 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12979 | Slave11 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12980 | Slave11 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12981 | Slave11 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12982 | Slave11 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12983 | Slave11 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12984 | Slave11 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12985 | Slave11 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12986 | Slave11 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12987 | Slave11 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12988 | Slave11 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12989 | Slave11 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12990 | Slave11 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12991 | Slave11 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12992 | Slave11 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12993 | Slave11 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12994 | Slave11 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12995 | Slave11 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12996 | Slave11 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12997 | Slave11 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12998 | Slave11 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
12999 | Slave11 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13000 | Slave11 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13001 | Slave11 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13002 | Slave11 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13003 | Slave11 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13004 | Slave11 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13005 | Slave11 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13006 | Slave11 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13007 | Slave11 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13008 | Slave11 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13009 | Slave11 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13010 | Slave11 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13011 | Slave11 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13012 | Slave11 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13013 | Slave11 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13014 | Slave11 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13015 | Slave11 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13016 | Slave11 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13017 | Slave11 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13018 | Slave11 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13019 | Slave11 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13020 | Slave11 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13021 | Slave11 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13022 | Slave11 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13023 | Slave11 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13024 | Slave12 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13025 | Slave12 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13026 | Slave12 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13027 | Slave12 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13028 | Slave12 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13029 | Slave12 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13030 | Slave12 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13031 | Slave12 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13032 | Slave12 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13033 | Slave12 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13034 | Slave12 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13035 | Slave12 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13036 | Slave12 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13037 | Slave12 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13038 | Slave12 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13039 | Slave12 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13040 | Slave12 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13041 | Slave12 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13042 | Slave12 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13043 | Slave12 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13044 | Slave12 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13045 | Slave12 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13046 | Slave12 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13047 | Slave12 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13048 | Slave12 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13049 | Slave12 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13050 | Slave12 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13051 | Slave12 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13052 | Slave12 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13053 | Slave12 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13054 | Slave12 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13055 | Slave12 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13056 | Slave12 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13057 | Slave12 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13058 | Slave12 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13059 | Slave12 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13060 | Slave12 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13061 | Slave12 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13062 | Slave12 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13063 | Slave12 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13064 | Slave12 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13065 | Slave12 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13066 | Slave12 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13067 | Slave12 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13068 | Slave12 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13069 | Slave12 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13070 | Slave12 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13071 | Slave12 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13072 | Slave13 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13073 | Slave13 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13074 | Slave13 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13075 | Slave13 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13076 | Slave13 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13077 | Slave13 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13078 | Slave13 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13079 | Slave13 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13080 | Slave13 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13081 | Slave13 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13082 | Slave13 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13083 | Slave13 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13084 | Slave13 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13085 | Slave13 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13086 | Slave13 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13087 | Slave13 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13088 | Slave13 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13089 | Slave13 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13090 | Slave13 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13091 | Slave13 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13092 | Slave13 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13093 | Slave13 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13094 | Slave13 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13095 | Slave13 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13096 | Slave13 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13097 | Slave13 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13098 | Slave13 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13099 | Slave13 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13100 | Slave13 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13101 | Slave13 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13102 | Slave13 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13103 | Slave13 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13104 | Slave13 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13105 | Slave13 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13106 | Slave13 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13107 | Slave13 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13108 | Slave13 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13109 | Slave13 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13110 | Slave13 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13111 | Slave13 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13112 | Slave13 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13113 | Slave13 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13114 | Slave13 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13115 | Slave13 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13116 | Slave13 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13117 | Slave13 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13118 | Slave13 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13119 | Slave13 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13120 | Slave14 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13121 | Slave14 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13122 | Slave14 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13123 | Slave14 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13124 | Slave14 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13125 | Slave14 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13126 | Slave14 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13127 | Slave14 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13128 | Slave14 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13129 | Slave14 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13130 | Slave14 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13131 | Slave14 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13132 | Slave14 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13133 | Slave14 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13134 | Slave14 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13135 | Slave14 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13136 | Slave14 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13137 | Slave14 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13138 | Slave14 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13139 | Slave14 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13140 | Slave14 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13141 | Slave14 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13142 | Slave14 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13143 | Slave14 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13144 | Slave14 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13145 | Slave14 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13146 | Slave14 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13147 | Slave14 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13148 | Slave14 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13149 | Slave14 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13150 | Slave14 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13151 | Slave14 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13152 | Slave14 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13153 | Slave14 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13154 | Slave14 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13155 | Slave14 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13156 | Slave14 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13157 | Slave14 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13158 | Slave14 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13159 | Slave14 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13160 | Slave14 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13161 | Slave14 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13162 | Slave14 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13163 | Slave14 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13164 | Slave14 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13165 | Slave14 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13166 | Slave14 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13167 | Slave14 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13168 | Slave15 Outlet Port01 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13169 | Slave15 Outlet Port02 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13170 | Slave15 Outlet Port03 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13171 | Slave15 Outlet Port04 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13172 | Slave15 Outlet Port05 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13173 | Slave15 Outlet Port06 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13174 | Slave15 Outlet Port07 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13175 | Slave15 Outlet Port08 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13176 | Slave15 Outlet Port09 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13177 | Slave15 Outlet Port10 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13178 | Slave15 Outlet Port11 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13179 | Slave15 Outlet Port12 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13180 | Slave15 Outlet Port13 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13181 | Slave15 Outlet Port14 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13182 | Slave15 Outlet Port15 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13183 | Slave15 Outlet Port16 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13184 | Slave15 Outlet Port17 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13185 | Slave15 Outlet Port18 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13186 | Slave15 Outlet Port19 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13187 | Slave15 Outlet Port20 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13188 | Slave15 Outlet Port21 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13189 | Slave15 Outlet Port22 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13190 | Slave15 Outlet Port23 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13191 | Slave15 Outlet Port24 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13192 | Slave15 Outlet Port25 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13193 | Slave15 Outlet Port26 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13194 | Slave15 Outlet Port27 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13195 | Slave15 Outlet Port28 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13196 | Slave15 Outlet Port29 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13197 | Slave15 Outlet Port30 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13198 | Slave15 Outlet Port31 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13199 | Slave15 Outlet Port32 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13200 | Slave15 Outlet Port33 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13201 | Slave15 Outlet Port34 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13202 | Slave15 Outlet Port35 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13203 | Slave15 Outlet Port36 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13204 | Slave15 Outlet Port37 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13205 | Slave15 Outlet Port38 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13206 | Slave15 Outlet Port39 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13207 | Slave15 Outlet Port40 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13208 | Slave15 Outlet Port41 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13209 | Slave15 Outlet Port42 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13210 | Slave15 Outlet Port43 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13211 | Slave15 Outlet Port44 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13212 | Slave15 Outlet Port45 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13213 | Slave15 Outlet Port46 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13214 | Slave15 Outlet Port47 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13215 | Slave15 Outlet Port48 Clear Energy | RW | 2 bytes | 1:Clear Energy; 0:Nothing
13216 | Master Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13217 | Master Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13218 | Master Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13219 | Master Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13220 | Master Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13221 | Master Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13222 | Master Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13223 | Master Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13224 | Master Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13225 | Master Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13226 | Master Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13227 | Master Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13228 | Master Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13229 | Master Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13230 | Master Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13231 | Master Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13232 | Master Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13233 | Master Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13234 | Master Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13235 | Master Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13236 | Master Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13237 | Master Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13238 | Master Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13239 | Master Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13240 | Master Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13241 | Master Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13242 | Master Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13243 | Master Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13244 | Master Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13245 | Master Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13246 | Master Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13247 | Master Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13248 | Master Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13249 | Master Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13250 | Master Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13251 | Master Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13252 | Master Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13253 | Master Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13254 | Master Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13255 | Master Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13256 | Master Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13257 | Master Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13258 | Master Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13259 | Master Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13260 | Master Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13261 | Master Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13262 | Master Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13263 | Master Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13264 | Slave01 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13265 | Slave01 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13266 | Slave01 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13267 | Slave01 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13268 | Slave01 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13269 | Slave01 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13270 | Slave01 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13271 | Slave01 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13272 | Slave01 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13273 | Slave01 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13274 | Slave01 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13275 | Slave01 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13276 | Slave01 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13277 | Slave01 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13278 | Slave01 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13279 | Slave01 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13280 | Slave01 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13281 | Slave01 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13282 | Slave01 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13283 | Slave01 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13284 | Slave01 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13285 | Slave01 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13286 | Slave01 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13287 | Slave01 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13288 | Slave01 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13289 | Slave01 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13290 | Slave01 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13291 | Slave01 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13292 | Slave01 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13293 | Slave01 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13294 | Slave01 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13295 | Slave01 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13296 | Slave01 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13297 | Slave01 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13298 | Slave01 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13299 | Slave01 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13300 | Slave01 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13301 | Slave01 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13302 | Slave01 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13303 | Slave01 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13304 | Slave01 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13305 | Slave01 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13306 | Slave01 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13307 | Slave01 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13308 | Slave01 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13309 | Slave01 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13310 | Slave01 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13311 | Slave01 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13312 | Slave02 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13313 | Slave02 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13314 | Slave02 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13315 | Slave02 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13316 | Slave02 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13317 | Slave02 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13318 | Slave02 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13319 | Slave02 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13320 | Slave02 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13321 | Slave02 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13322 | Slave02 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13323 | Slave02 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13324 | Slave02 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13325 | Slave02 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13326 | Slave02 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13327 | Slave02 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13328 | Slave02 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13329 | Slave02 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13330 | Slave02 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13331 | Slave02 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13332 | Slave02 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13333 | Slave02 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13334 | Slave02 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13335 | Slave02 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13336 | Slave02 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13337 | Slave02 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13338 | Slave02 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13339 | Slave02 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13340 | Slave02 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13341 | Slave02 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13342 | Slave02 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13343 | Slave02 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13344 | Slave02 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13345 | Slave02 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13346 | Slave02 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13347 | Slave02 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13348 | Slave02 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13349 | Slave02 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13350 | Slave02 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13351 | Slave02 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13352 | Slave02 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13353 | Slave02 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13354 | Slave02 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13355 | Slave02 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13356 | Slave02 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13357 | Slave02 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13358 | Slave02 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13359 | Slave02 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13360 | Slave03 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13361 | Slave03 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13362 | Slave03 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13363 | Slave03 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13364 | Slave03 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13365 | Slave03 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13366 | Slave03 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13367 | Slave03 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13368 | Slave03 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13369 | Slave03 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13370 | Slave03 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13371 | Slave03 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13372 | Slave03 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13373 | Slave03 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13374 | Slave03 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13375 | Slave03 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13376 | Slave03 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13377 | Slave03 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13378 | Slave03 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13379 | Slave03 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13380 | Slave03 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13381 | Slave03 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13382 | Slave03 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13383 | Slave03 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13384 | Slave03 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13385 | Slave03 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13386 | Slave03 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13387 | Slave03 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13388 | Slave03 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13389 | Slave03 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13390 | Slave03 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13391 | Slave03 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13392 | Slave03 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13393 | Slave03 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13394 | Slave03 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13395 | Slave03 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13396 | Slave03 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13397 | Slave03 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13398 | Slave03 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13399 | Slave03 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13400 | Slave03 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13401 | Slave03 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13402 | Slave03 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13403 | Slave03 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13404 | Slave03 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13405 | Slave03 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13406 | Slave03 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13407 | Slave03 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13408 | Slave04 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13409 | Slave04 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13410 | Slave04 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13411 | Slave04 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13412 | Slave04 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13413 | Slave04 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13414 | Slave04 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13415 | Slave04 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13416 | Slave04 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13417 | Slave04 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13418 | Slave04 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13419 | Slave04 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13420 | Slave04 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13421 | Slave04 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13422 | Slave04 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13423 | Slave04 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13424 | Slave04 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13425 | Slave04 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13426 | Slave04 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13427 | Slave04 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13428 | Slave04 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13429 | Slave04 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13430 | Slave04 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13431 | Slave04 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13432 | Slave04 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13433 | Slave04 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13434 | Slave04 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13435 | Slave04 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13436 | Slave04 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13437 | Slave04 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13438 | Slave04 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13439 | Slave04 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13440 | Slave04 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13441 | Slave04 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13442 | Slave04 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13443 | Slave04 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13444 | Slave04 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13445 | Slave04 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13446 | Slave04 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13447 | Slave04 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13448 | Slave04 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13449 | Slave04 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13450 | Slave04 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13451 | Slave04 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13452 | Slave04 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13453 | Slave04 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13454 | Slave04 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13455 | Slave04 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13456 | Slave05 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13457 | Slave05 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13458 | Slave05 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13459 | Slave05 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13460 | Slave05 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13461 | Slave05 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13462 | Slave05 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13463 | Slave05 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13464 | Slave05 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13465 | Slave05 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13466 | Slave05 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13467 | Slave05 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13468 | Slave05 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13469 | Slave05 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13470 | Slave05 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13471 | Slave05 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13472 | Slave05 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13473 | Slave05 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13474 | Slave05 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13475 | Slave05 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13476 | Slave05 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13477 | Slave05 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13478 | Slave05 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13479 | Slave05 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13480 | Slave05 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13481 | Slave05 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13482 | Slave05 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13483 | Slave05 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13484 | Slave05 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13485 | Slave05 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13486 | Slave05 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13487 | Slave05 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13488 | Slave05 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13489 | Slave05 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13490 | Slave05 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13491 | Slave05 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13492 | Slave05 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13493 | Slave05 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13494 | Slave05 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13495 | Slave05 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13496 | Slave05 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13497 | Slave05 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13498 | Slave05 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13499 | Slave05 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13500 | Slave05 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13501 | Slave05 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13502 | Slave05 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13503 | Slave05 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13504 | Slave06 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13505 | Slave06 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13506 | Slave06 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13507 | Slave06 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13508 | Slave06 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13509 | Slave06 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13510 | Slave06 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13511 | Slave06 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13512 | Slave06 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13513 | Slave06 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13514 | Slave06 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13515 | Slave06 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13516 | Slave06 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13517 | Slave06 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13518 | Slave06 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13519 | Slave06 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13520 | Slave06 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13521 | Slave06 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13522 | Slave06 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13523 | Slave06 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13524 | Slave06 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13525 | Slave06 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13526 | Slave06 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13527 | Slave06 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13528 | Slave06 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13529 | Slave06 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13530 | Slave06 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13531 | Slave06 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13532 | Slave06 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13533 | Slave06 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13534 | Slave06 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13535 | Slave06 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13536 | Slave06 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13537 | Slave06 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13538 | Slave06 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13539 | Slave06 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13540 | Slave06 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13541 | Slave06 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13542 | Slave06 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13543 | Slave06 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13544 | Slave06 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13545 | Slave06 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13546 | Slave06 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13547 | Slave06 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13548 | Slave06 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13549 | Slave06 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13550 | Slave06 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13551 | Slave06 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13552 | Slave07 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13553 | Slave07 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13554 | Slave07 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13555 | Slave07 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13556 | Slave07 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13557 | Slave07 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13558 | Slave07 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13559 | Slave07 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13560 | Slave07 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13561 | Slave07 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13562 | Slave07 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13563 | Slave07 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13564 | Slave07 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13565 | Slave07 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13566 | Slave07 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13567 | Slave07 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13568 | Slave07 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13569 | Slave07 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13570 | Slave07 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13571 | Slave07 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13572 | Slave07 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13573 | Slave07 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13574 | Slave07 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13575 | Slave07 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13576 | Slave07 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13577 | Slave07 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13578 | Slave07 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13579 | Slave07 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13580 | Slave07 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13581 | Slave07 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13582 | Slave07 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13583 | Slave07 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13584 | Slave07 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13585 | Slave07 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13586 | Slave07 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13587 | Slave07 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13588 | Slave07 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13589 | Slave07 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13590 | Slave07 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13591 | Slave07 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13592 | Slave07 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13593 | Slave07 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13594 | Slave07 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13595 | Slave07 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13596 | Slave07 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13597 | Slave07 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13598 | Slave07 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13599 | Slave07 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13600 | Slave08 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13601 | Slave08 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13602 | Slave08 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13603 | Slave08 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13604 | Slave08 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13605 | Slave08 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13606 | Slave08 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13607 | Slave08 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13608 | Slave08 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13609 | Slave08 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13610 | Slave08 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13611 | Slave08 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13612 | Slave08 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13613 | Slave08 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13614 | Slave08 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13615 | Slave08 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13616 | Slave08 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13617 | Slave08 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13618 | Slave08 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13619 | Slave08 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13620 | Slave08 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13621 | Slave08 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13622 | Slave08 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13623 | Slave08 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13624 | Slave08 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13625 | Slave08 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13626 | Slave08 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13627 | Slave08 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13628 | Slave08 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13629 | Slave08 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13630 | Slave08 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13631 | Slave08 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13632 | Slave08 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13633 | Slave08 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13634 | Slave08 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13635 | Slave08 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13636 | Slave08 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13637 | Slave08 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13638 | Slave08 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13639 | Slave08 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13640 | Slave08 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13641 | Slave08 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13642 | Slave08 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13643 | Slave08 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13644 | Slave08 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13645 | Slave08 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13646 | Slave08 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13647 | Slave08 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13648 | Slave09 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13649 | Slave09 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13650 | Slave09 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13651 | Slave09 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13652 | Slave09 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13653 | Slave09 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13654 | Slave09 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13655 | Slave09 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13656 | Slave09 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13657 | Slave09 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13658 | Slave09 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13659 | Slave09 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13660 | Slave09 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13661 | Slave09 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13662 | Slave09 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13663 | Slave09 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13664 | Slave09 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13665 | Slave09 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13666 | Slave09 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13667 | Slave09 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13668 | Slave09 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13669 | Slave09 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13670 | Slave09 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13671 | Slave09 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13672 | Slave09 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13673 | Slave09 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13674 | Slave09 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13675 | Slave09 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13676 | Slave09 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13677 | Slave09 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13678 | Slave09 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13679 | Slave09 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13680 | Slave09 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13681 | Slave09 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13682 | Slave09 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13683 | Slave09 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13684 | Slave09 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13685 | Slave09 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13686 | Slave09 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13687 | Slave09 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13688 | Slave09 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13689 | Slave09 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13690 | Slave09 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13691 | Slave09 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13692 | Slave09 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13693 | Slave09 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13694 | Slave09 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13695 | Slave09 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13696 | Slave10 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13697 | Slave10 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13698 | Slave10 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13699 | Slave10 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13700 | Slave10 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13701 | Slave10 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13702 | Slave10 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13703 | Slave10 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13704 | Slave10 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13705 | Slave10 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13706 | Slave10 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13707 | Slave10 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13708 | Slave10 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13709 | Slave10 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13710 | Slave10 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13711 | Slave10 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13712 | Slave10 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13713 | Slave10 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13714 | Slave10 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13715 | Slave10 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13716 | Slave10 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13717 | Slave10 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13718 | Slave10 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13719 | Slave10 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13720 | Slave10 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13721 | Slave10 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13722 | Slave10 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13723 | Slave10 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13724 | Slave10 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13725 | Slave10 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13726 | Slave10 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13727 | Slave10 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13728 | Slave10 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13729 | Slave10 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13730 | Slave10 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13731 | Slave10 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13732 | Slave10 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13733 | Slave10 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13734 | Slave10 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13735 | Slave10 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13736 | Slave10 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13737 | Slave10 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13738 | Slave10 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13739 | Slave10 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13740 | Slave10 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13741 | Slave10 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13742 | Slave10 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13743 | Slave10 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13744 | Slave11 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13745 | Slave11 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13746 | Slave11 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13747 | Slave11 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13748 | Slave11 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13749 | Slave11 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13750 | Slave11 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13751 | Slave11 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13752 | Slave11 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13753 | Slave11 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13754 | Slave11 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13755 | Slave11 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13756 | Slave11 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13757 | Slave11 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13758 | Slave11 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13759 | Slave11 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13760 | Slave11 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13761 | Slave11 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13762 | Slave11 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13763 | Slave11 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13764 | Slave11 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13765 | Slave11 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13766 | Slave11 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13767 | Slave11 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13768 | Slave11 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13769 | Slave11 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13770 | Slave11 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13771 | Slave11 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13772 | Slave11 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13773 | Slave11 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13774 | Slave11 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13775 | Slave11 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13776 | Slave11 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13777 | Slave11 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13778 | Slave11 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13779 | Slave11 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13780 | Slave11 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13781 | Slave11 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13782 | Slave11 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13783 | Slave11 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13784 | Slave11 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13785 | Slave11 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13786 | Slave11 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13787 | Slave11 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13788 | Slave11 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13789 | Slave11 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13790 | Slave11 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13791 | Slave11 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13792 | Slave12 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13793 | Slave12 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13794 | Slave12 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13795 | Slave12 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13796 | Slave12 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13797 | Slave12 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13798 | Slave12 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13799 | Slave12 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13800 | Slave12 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13801 | Slave12 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13802 | Slave12 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13803 | Slave12 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13804 | Slave12 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13805 | Slave12 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13806 | Slave12 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13807 | Slave12 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13808 | Slave12 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13809 | Slave12 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13810 | Slave12 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13811 | Slave12 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13812 | Slave12 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13813 | Slave12 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13814 | Slave12 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13815 | Slave12 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13816 | Slave12 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13817 | Slave12 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13818 | Slave12 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13819 | Slave12 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13820 | Slave12 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13821 | Slave12 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13822 | Slave12 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13823 | Slave12 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13824 | Slave12 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13825 | Slave12 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13826 | Slave12 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13827 | Slave12 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13828 | Slave12 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13829 | Slave12 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13830 | Slave12 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13831 | Slave12 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13832 | Slave12 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13833 | Slave12 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13834 | Slave12 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13835 | Slave12 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13836 | Slave12 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13837 | Slave12 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13838 | Slave12 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13839 | Slave12 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13840 | Slave13 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13841 | Slave13 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13842 | Slave13 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13843 | Slave13 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13844 | Slave13 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13845 | Slave13 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13846 | Slave13 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13847 | Slave13 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13848 | Slave13 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13849 | Slave13 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13850 | Slave13 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13851 | Slave13 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13852 | Slave13 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13853 | Slave13 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13854 | Slave13 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13855 | Slave13 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13856 | Slave13 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13857 | Slave13 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13858 | Slave13 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13859 | Slave13 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13860 | Slave13 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13861 | Slave13 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13862 | Slave13 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13863 | Slave13 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13864 | Slave13 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13865 | Slave13 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13866 | Slave13 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13867 | Slave13 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13868 | Slave13 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13869 | Slave13 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13870 | Slave13 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13871 | Slave13 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13872 | Slave13 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13873 | Slave13 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13874 | Slave13 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13875 | Slave13 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13876 | Slave13 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13877 | Slave13 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13878 | Slave13 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13879 | Slave13 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13880 | Slave13 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13881 | Slave13 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13882 | Slave13 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13883 | Slave13 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13884 | Slave13 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13885 | Slave13 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13886 | Slave13 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13887 | Slave13 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13888 | Slave14 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13889 | Slave14 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13890 | Slave14 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13891 | Slave14 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13892 | Slave14 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13893 | Slave14 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13894 | Slave14 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13895 | Slave14 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13896 | Slave14 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13897 | Slave14 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13898 | Slave14 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13899 | Slave14 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13900 | Slave14 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13901 | Slave14 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13902 | Slave14 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13903 | Slave14 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13904 | Slave14 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13905 | Slave14 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13906 | Slave14 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13907 | Slave14 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13908 | Slave14 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13909 | Slave14 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13910 | Slave14 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13911 | Slave14 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13912 | Slave14 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13913 | Slave14 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13914 | Slave14 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13915 | Slave14 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13916 | Slave14 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13917 | Slave14 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13918 | Slave14 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13919 | Slave14 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13920 | Slave14 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13921 | Slave14 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13922 | Slave14 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13923 | Slave14 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13924 | Slave14 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13925 | Slave14 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13926 | Slave14 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13927 | Slave14 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13928 | Slave14 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13929 | Slave14 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13930 | Slave14 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13931 | Slave14 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13932 | Slave14 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13933 | Slave14 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13934 | Slave14 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13935 | Slave14 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13936 | Slave15 Outlet Port01 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13937 | Slave15 Outlet Port02 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13938 | Slave15 Outlet Port03 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13939 | Slave15 Outlet Port04 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13940 | Slave15 Outlet Port05 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13941 | Slave15 Outlet Port06 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13942 | Slave15 Outlet Port07 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13943 | Slave15 Outlet Port08 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13944 | Slave15 Outlet Port09 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13945 | Slave15 Outlet Port10 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13946 | Slave15 Outlet Port11 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13947 | Slave15 Outlet Port12 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13948 | Slave15 Outlet Port13 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13949 | Slave15 Outlet Port14 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13950 | Slave15 Outlet Port15 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13951 | Slave15 Outlet Port16 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13952 | Slave15 Outlet Port17 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13953 | Slave15 Outlet Port18 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13954 | Slave15 Outlet Port19 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13955 | Slave15 Outlet Port20 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13956 | Slave15 Outlet Port21 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13957 | Slave15 Outlet Port22 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13958 | Slave15 Outlet Port23 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13959 | Slave15 Outlet Port24 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13960 | Slave15 Outlet Port25 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13961 | Slave15 Outlet Port26 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13962 | Slave15 Outlet Port27 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13963 | Slave15 Outlet Port28 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13964 | Slave15 Outlet Port29 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13965 | Slave15 Outlet Port30 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13966 | Slave15 Outlet Port31 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13967 | Slave15 Outlet Port32 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13968 | Slave15 Outlet Port33 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13969 | Slave15 Outlet Port34 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13970 | Slave15 Outlet Port35 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13971 | Slave15 Outlet Port36 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13972 | Slave15 Outlet Port37 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13973 | Slave15 Outlet Port38 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13974 | Slave15 Outlet Port39 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13975 | Slave15 Outlet Port40 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13976 | Slave15 Outlet Port41 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13977 | Slave15 Outlet Port42 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13978 | Slave15 Outlet Port43 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13979 | Slave15 Outlet Port44 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13980 | Slave15 Outlet Port45 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13981 | Slave15 Outlet Port46 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13982 | Slave15 Outlet Port47 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13983 | Slave15 Outlet Port48 On Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13984 | Master Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13985 | Master Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13986 | Master Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13987 | Master Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13988 | Master Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13989 | Master Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13990 | Master Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13991 | Master Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13992 | Master Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13993 | Master Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13994 | Master Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13995 | Master Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13996 | Master Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13997 | Master Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13998 | Master Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
13999 | Master Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14000 | Master Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14001 | Master Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14002 | Master Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14003 | Master Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14004 | Master Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14005 | Master Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14006 | Master Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14007 | Master Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14008 | Master Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14009 | Master Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14010 | Master Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14011 | Master Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14012 | Master Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14013 | Master Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14014 | Master Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14015 | Master Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14016 | Master Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14017 | Master Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14018 | Master Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14019 | Master Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14020 | Master Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14021 | Master Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14022 | Master Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14023 | Master Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14024 | Master Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14025 | Master Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14026 | Master Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14027 | Master Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14028 | Master Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14029 | Master Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14030 | Master Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14031 | Master Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14032 | Slave01 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14033 | Slave01 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14034 | Slave01 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14035 | Slave01 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14036 | Slave01 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14037 | Slave01 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14038 | Slave01 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14039 | Slave01 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14040 | Slave01 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14041 | Slave01 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14042 | Slave01 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14043 | Slave01 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14044 | Slave01 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14045 | Slave01 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14046 | Slave01 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14047 | Slave01 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14048 | Slave01 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14049 | Slave01 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14050 | Slave01 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14051 | Slave01 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14052 | Slave01 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14053 | Slave01 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14054 | Slave01 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14055 | Slave01 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14056 | Slave01 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14057 | Slave01 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14058 | Slave01 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14059 | Slave01 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14060 | Slave01 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14061 | Slave01 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14062 | Slave01 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14063 | Slave01 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14064 | Slave01 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14065 | Slave01 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14066 | Slave01 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14067 | Slave01 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14068 | Slave01 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14069 | Slave01 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14070 | Slave01 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14071 | Slave01 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14072 | Slave01 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14073 | Slave01 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14074 | Slave01 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14075 | Slave01 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14076 | Slave01 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14077 | Slave01 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14078 | Slave01 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14079 | Slave01 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14080 | Slave02 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14081 | Slave02 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14082 | Slave02 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14083 | Slave02 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14084 | Slave02 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14085 | Slave02 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14086 | Slave02 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14087 | Slave02 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14088 | Slave02 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14089 | Slave02 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14090 | Slave02 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14091 | Slave02 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14092 | Slave02 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14093 | Slave02 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14094 | Slave02 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14095 | Slave02 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14096 | Slave02 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14097 | Slave02 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14098 | Slave02 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14099 | Slave02 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14100 | Slave02 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14101 | Slave02 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14102 | Slave02 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14103 | Slave02 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14104 | Slave02 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14105 | Slave02 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14106 | Slave02 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14107 | Slave02 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14108 | Slave02 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14109 | Slave02 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14110 | Slave02 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14111 | Slave02 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14112 | Slave02 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14113 | Slave02 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14114 | Slave02 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14115 | Slave02 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14116 | Slave02 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14117 | Slave02 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14118 | Slave02 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14119 | Slave02 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14120 | Slave02 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14121 | Slave02 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14122 | Slave02 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14123 | Slave02 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14124 | Slave02 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14125 | Slave02 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14126 | Slave02 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14127 | Slave02 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14128 | Slave03 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14129 | Slave03 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14130 | Slave03 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14131 | Slave03 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14132 | Slave03 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14133 | Slave03 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14134 | Slave03 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14135 | Slave03 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14136 | Slave03 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14137 | Slave03 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14138 | Slave03 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14139 | Slave03 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14140 | Slave03 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14141 | Slave03 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14142 | Slave03 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14143 | Slave03 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14144 | Slave03 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14145 | Slave03 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14146 | Slave03 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14147 | Slave03 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14148 | Slave03 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14149 | Slave03 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14150 | Slave03 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14151 | Slave03 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14152 | Slave03 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14153 | Slave03 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14154 | Slave03 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14155 | Slave03 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14156 | Slave03 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14157 | Slave03 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14158 | Slave03 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14159 | Slave03 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14160 | Slave03 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14161 | Slave03 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14162 | Slave03 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14163 | Slave03 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14164 | Slave03 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14165 | Slave03 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14166 | Slave03 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14167 | Slave03 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14168 | Slave03 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14169 | Slave03 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14170 | Slave03 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14171 | Slave03 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14172 | Slave03 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14173 | Slave03 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14174 | Slave03 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14175 | Slave03 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14176 | Slave04 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14177 | Slave04 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14178 | Slave04 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14179 | Slave04 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14180 | Slave04 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14181 | Slave04 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14182 | Slave04 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14183 | Slave04 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14184 | Slave04 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14185 | Slave04 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14186 | Slave04 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14187 | Slave04 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14188 | Slave04 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14189 | Slave04 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14190 | Slave04 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14191 | Slave04 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14192 | Slave04 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14193 | Slave04 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14194 | Slave04 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14195 | Slave04 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14196 | Slave04 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14197 | Slave04 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14198 | Slave04 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14199 | Slave04 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14200 | Slave04 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14201 | Slave04 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14202 | Slave04 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14203 | Slave04 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14204 | Slave04 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14205 | Slave04 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14206 | Slave04 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14207 | Slave04 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14208 | Slave04 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14209 | Slave04 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14210 | Slave04 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14211 | Slave04 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14212 | Slave04 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14213 | Slave04 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14214 | Slave04 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14215 | Slave04 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14216 | Slave04 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14217 | Slave04 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14218 | Slave04 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14219 | Slave04 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14220 | Slave04 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14221 | Slave04 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14222 | Slave04 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14223 | Slave04 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14224 | Slave05 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14225 | Slave05 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14226 | Slave05 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14227 | Slave05 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14228 | Slave05 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14229 | Slave05 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14230 | Slave05 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14231 | Slave05 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14232 | Slave05 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14233 | Slave05 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14234 | Slave05 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14235 | Slave05 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14236 | Slave05 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14237 | Slave05 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14238 | Slave05 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14239 | Slave05 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14240 | Slave05 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14241 | Slave05 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14242 | Slave05 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14243 | Slave05 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14244 | Slave05 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14245 | Slave05 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14246 | Slave05 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14247 | Slave05 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14248 | Slave05 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14249 | Slave05 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14250 | Slave05 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14251 | Slave05 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14252 | Slave05 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14253 | Slave05 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14254 | Slave05 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14255 | Slave05 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14256 | Slave05 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14257 | Slave05 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14258 | Slave05 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14259 | Slave05 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14260 | Slave05 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14261 | Slave05 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14262 | Slave05 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14263 | Slave05 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14264 | Slave05 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14265 | Slave05 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14266 | Slave05 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14267 | Slave05 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14268 | Slave05 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14269 | Slave05 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14270 | Slave05 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14271 | Slave05 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14272 | Slave06 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14273 | Slave06 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14274 | Slave06 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14275 | Slave06 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14276 | Slave06 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14277 | Slave06 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14278 | Slave06 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14279 | Slave06 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14280 | Slave06 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14281 | Slave06 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14282 | Slave06 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14283 | Slave06 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14284 | Slave06 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14285 | Slave06 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14286 | Slave06 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14287 | Slave06 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14288 | Slave06 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14289 | Slave06 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14290 | Slave06 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14291 | Slave06 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14292 | Slave06 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14293 | Slave06 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14294 | Slave06 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14295 | Slave06 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14296 | Slave06 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14297 | Slave06 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14298 | Slave06 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14299 | Slave06 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14300 | Slave06 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14301 | Slave06 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14302 | Slave06 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14303 | Slave06 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14304 | Slave06 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14305 | Slave06 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14306 | Slave06 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14307 | Slave06 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14308 | Slave06 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14309 | Slave06 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14310 | Slave06 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14311 | Slave06 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14312 | Slave06 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14313 | Slave06 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14314 | Slave06 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14315 | Slave06 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14316 | Slave06 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14317 | Slave06 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14318 | Slave06 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14319 | Slave06 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14320 | Slave07 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14321 | Slave07 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14322 | Slave07 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14323 | Slave07 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14324 | Slave07 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14325 | Slave07 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14326 | Slave07 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14327 | Slave07 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14328 | Slave07 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14329 | Slave07 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14330 | Slave07 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14331 | Slave07 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14332 | Slave07 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14333 | Slave07 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14334 | Slave07 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14335 | Slave07 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14336 | Slave07 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14337 | Slave07 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14338 | Slave07 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14339 | Slave07 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14340 | Slave07 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14341 | Slave07 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14342 | Slave07 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14343 | Slave07 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14344 | Slave07 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14345 | Slave07 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14346 | Slave07 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14347 | Slave07 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14348 | Slave07 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14349 | Slave07 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14350 | Slave07 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14351 | Slave07 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14352 | Slave07 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14353 | Slave07 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14354 | Slave07 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14355 | Slave07 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14356 | Slave07 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14357 | Slave07 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14358 | Slave07 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14359 | Slave07 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14360 | Slave07 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14361 | Slave07 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14362 | Slave07 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14363 | Slave07 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14364 | Slave07 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14365 | Slave07 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14366 | Slave07 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14367 | Slave07 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14368 | Slave08 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14369 | Slave08 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14370 | Slave08 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14371 | Slave08 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14372 | Slave08 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14373 | Slave08 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14374 | Slave08 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14375 | Slave08 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14376 | Slave08 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14377 | Slave08 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14378 | Slave08 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14379 | Slave08 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14380 | Slave08 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14381 | Slave08 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14382 | Slave08 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14383 | Slave08 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14384 | Slave08 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14385 | Slave08 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14386 | Slave08 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14387 | Slave08 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14388 | Slave08 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14389 | Slave08 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14390 | Slave08 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14391 | Slave08 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14392 | Slave08 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14393 | Slave08 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14394 | Slave08 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14395 | Slave08 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14396 | Slave08 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14397 | Slave08 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14398 | Slave08 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14399 | Slave08 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14400 | Slave08 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14401 | Slave08 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14402 | Slave08 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14403 | Slave08 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14404 | Slave08 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14405 | Slave08 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14406 | Slave08 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14407 | Slave08 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14408 | Slave08 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14409 | Slave08 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14410 | Slave08 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14411 | Slave08 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14412 | Slave08 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14413 | Slave08 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14414 | Slave08 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14415 | Slave08 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14416 | Slave09 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14417 | Slave09 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14418 | Slave09 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14419 | Slave09 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14420 | Slave09 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14421 | Slave09 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14422 | Slave09 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14423 | Slave09 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14424 | Slave09 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14425 | Slave09 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14426 | Slave09 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14427 | Slave09 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14428 | Slave09 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14429 | Slave09 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14430 | Slave09 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14431 | Slave09 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14432 | Slave09 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14433 | Slave09 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14434 | Slave09 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14435 | Slave09 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14436 | Slave09 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14437 | Slave09 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14438 | Slave09 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14439 | Slave09 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14440 | Slave09 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14441 | Slave09 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14442 | Slave09 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14443 | Slave09 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14444 | Slave09 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14445 | Slave09 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14446 | Slave09 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14447 | Slave09 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14448 | Slave09 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14449 | Slave09 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14450 | Slave09 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14451 | Slave09 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14452 | Slave09 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14453 | Slave09 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14454 | Slave09 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14455 | Slave09 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14456 | Slave09 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14457 | Slave09 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14458 | Slave09 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14459 | Slave09 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14460 | Slave09 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14461 | Slave09 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14462 | Slave09 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14463 | Slave09 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14464 | Slave10 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14465 | Slave10 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14466 | Slave10 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14467 | Slave10 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14468 | Slave10 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14469 | Slave10 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14470 | Slave10 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14471 | Slave10 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14472 | Slave10 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14473 | Slave10 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14474 | Slave10 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14475 | Slave10 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14476 | Slave10 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14477 | Slave10 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14478 | Slave10 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14479 | Slave10 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14480 | Slave10 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14481 | Slave10 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14482 | Slave10 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14483 | Slave10 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14484 | Slave10 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14485 | Slave10 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14486 | Slave10 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14487 | Slave10 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14488 | Slave10 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14489 | Slave10 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14490 | Slave10 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14491 | Slave10 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14492 | Slave10 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14493 | Slave10 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14494 | Slave10 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14495 | Slave10 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14496 | Slave10 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14497 | Slave10 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14498 | Slave10 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14499 | Slave10 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14500 | Slave10 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14501 | Slave10 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14502 | Slave10 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14503 | Slave10 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14504 | Slave10 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14505 | Slave10 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14506 | Slave10 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14507 | Slave10 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14508 | Slave10 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14509 | Slave10 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14510 | Slave10 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14511 | Slave10 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14512 | Slave11 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14513 | Slave11 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14514 | Slave11 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14515 | Slave11 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14516 | Slave11 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14517 | Slave11 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14518 | Slave11 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14519 | Slave11 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14520 | Slave11 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14521 | Slave11 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14522 | Slave11 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14523 | Slave11 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14524 | Slave11 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14525 | Slave11 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14526 | Slave11 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14527 | Slave11 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14528 | Slave11 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14529 | Slave11 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14530 | Slave11 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14531 | Slave11 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14532 | Slave11 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14533 | Slave11 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14534 | Slave11 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14535 | Slave11 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14536 | Slave11 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14537 | Slave11 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14538 | Slave11 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14539 | Slave11 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14540 | Slave11 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14541 | Slave11 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14542 | Slave11 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14543 | Slave11 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14544 | Slave11 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14545 | Slave11 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14546 | Slave11 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14547 | Slave11 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14548 | Slave11 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14549 | Slave11 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14550 | Slave11 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14551 | Slave11 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14552 | Slave11 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14553 | Slave11 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14554 | Slave11 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14555 | Slave11 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14556 | Slave11 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14557 | Slave11 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14558 | Slave11 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14559 | Slave11 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14560 | Slave12 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14561 | Slave12 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14562 | Slave12 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14563 | Slave12 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14564 | Slave12 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14565 | Slave12 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14566 | Slave12 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14567 | Slave12 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14568 | Slave12 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14569 | Slave12 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14570 | Slave12 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14571 | Slave12 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14572 | Slave12 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14573 | Slave12 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14574 | Slave12 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14575 | Slave12 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14576 | Slave12 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14577 | Slave12 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14578 | Slave12 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14579 | Slave12 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14580 | Slave12 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14581 | Slave12 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14582 | Slave12 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14583 | Slave12 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14584 | Slave12 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14585 | Slave12 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14586 | Slave12 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14587 | Slave12 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14588 | Slave12 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14589 | Slave12 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14590 | Slave12 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14591 | Slave12 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14592 | Slave12 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14593 | Slave12 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14594 | Slave12 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14595 | Slave12 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14596 | Slave12 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14597 | Slave12 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14598 | Slave12 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14599 | Slave12 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14600 | Slave12 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14601 | Slave12 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14602 | Slave12 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14603 | Slave12 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14604 | Slave12 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14605 | Slave12 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14606 | Slave12 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14607 | Slave12 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14608 | Slave13 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14609 | Slave13 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14610 | Slave13 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14611 | Slave13 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14612 | Slave13 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14613 | Slave13 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14614 | Slave13 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14615 | Slave13 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14616 | Slave13 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14617 | Slave13 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14618 | Slave13 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14619 | Slave13 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14620 | Slave13 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14621 | Slave13 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14622 | Slave13 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14623 | Slave13 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14624 | Slave13 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14625 | Slave13 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14626 | Slave13 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14627 | Slave13 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14628 | Slave13 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14629 | Slave13 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14630 | Slave13 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14631 | Slave13 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14632 | Slave13 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14633 | Slave13 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14634 | Slave13 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14635 | Slave13 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14636 | Slave13 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14637 | Slave13 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14638 | Slave13 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14639 | Slave13 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14640 | Slave13 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14641 | Slave13 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14642 | Slave13 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14643 | Slave13 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14644 | Slave13 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14645 | Slave13 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14646 | Slave13 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14647 | Slave13 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14648 | Slave13 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14649 | Slave13 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14650 | Slave13 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14651 | Slave13 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14652 | Slave13 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14653 | Slave13 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14654 | Slave13 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14655 | Slave13 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14656 | Slave14 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14657 | Slave14 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14658 | Slave14 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14659 | Slave14 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14660 | Slave14 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14661 | Slave14 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14662 | Slave14 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14663 | Slave14 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14664 | Slave14 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14665 | Slave14 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14666 | Slave14 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14667 | Slave14 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14668 | Slave14 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14669 | Slave14 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14670 | Slave14 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14671 | Slave14 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14672 | Slave14 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14673 | Slave14 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14674 | Slave14 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14675 | Slave14 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14676 | Slave14 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14677 | Slave14 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14678 | Slave14 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14679 | Slave14 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14680 | Slave14 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14681 | Slave14 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14682 | Slave14 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14683 | Slave14 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14684 | Slave14 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14685 | Slave14 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14686 | Slave14 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14687 | Slave14 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14688 | Slave14 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14689 | Slave14 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14690 | Slave14 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14691 | Slave14 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14692 | Slave14 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14693 | Slave14 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14694 | Slave14 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14695 | Slave14 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14696 | Slave14 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14697 | Slave14 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14698 | Slave14 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14699 | Slave14 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14700 | Slave14 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14701 | Slave14 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14702 | Slave14 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14703 | Slave14 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14704 | Slave15 Outlet Port01 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14705 | Slave15 Outlet Port02 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14706 | Slave15 Outlet Port03 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14707 | Slave15 Outlet Port04 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14708 | Slave15 Outlet Port05 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14709 | Slave15 Outlet Port06 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14710 | Slave15 Outlet Port07 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14711 | Slave15 Outlet Port08 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14712 | Slave15 Outlet Port09 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14713 | Slave15 Outlet Port10 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14714 | Slave15 Outlet Port11 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14715 | Slave15 Outlet Port12 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14716 | Slave15 Outlet Port13 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14717 | Slave15 Outlet Port14 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14718 | Slave15 Outlet Port15 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14719 | Slave15 Outlet Port16 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14720 | Slave15 Outlet Port17 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14721 | Slave15 Outlet Port18 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14722 | Slave15 Outlet Port19 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14723 | Slave15 Outlet Port20 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14724 | Slave15 Outlet Port21 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14725 | Slave15 Outlet Port22 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14726 | Slave15 Outlet Port23 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14727 | Slave15 Outlet Port24 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14728 | Slave15 Outlet Port25 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14729 | Slave15 Outlet Port26 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14730 | Slave15 Outlet Port27 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14731 | Slave15 Outlet Port28 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14732 | Slave15 Outlet Port29 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14733 | Slave15 Outlet Port30 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14734 | Slave15 Outlet Port31 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14735 | Slave15 Outlet Port32 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14736 | Slave15 Outlet Port33 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14737 | Slave15 Outlet Port34 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14738 | Slave15 Outlet Port35 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14739 | Slave15 Outlet Port36 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14740 | Slave15 Outlet Port37 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14741 | Slave15 Outlet Port38 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14742 | Slave15 Outlet Port39 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14743 | Slave15 Outlet Port40 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14744 | Slave15 Outlet Port41 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14745 | Slave15 Outlet Port42 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14746 | Slave15 Outlet Port43 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14747 | Slave15 Outlet Port44 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14748 | Slave15 Outlet Port45 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14749 | Slave15 Outlet Port46 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14750 | Slave15 Outlet Port47 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14751 | Slave15 Outlet Port48 Off Delay Time | RW | 2 bytes | Range is 0 ~ 7200
14752 | Master Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14753 | Master Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14754 | Master Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14755 | Master Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14756 | Master Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14757 | Master Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14758 | Master Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14759 | Master Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14760 | Master Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14761 | Master Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14762 | Master Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14763 | Master Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14764 | Master Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14765 | Master Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14766 | Master Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14767 | Master Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14768 | Master Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14769 | Master Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14770 | Master Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14771 | Master Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14772 | Master Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14773 | Master Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14774 | Master Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14775 | Master Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14776 | Master Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14777 | Master Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14778 | Master Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14779 | Master Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14780 | Master Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14781 | Master Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14782 | Master Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14783 | Master Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14784 | Master Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14785 | Master Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14786 | Master Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14787 | Master Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14788 | Master Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14789 | Master Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14790 | Master Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14791 | Master Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14792 | Master Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14793 | Master Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14794 | Master Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14795 | Master Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14796 | Master Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14797 | Master Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14798 | Master Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14799 | Master Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14800 | Slave01 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14801 | Slave01 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14802 | Slave01 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14803 | Slave01 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14804 | Slave01 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14805 | Slave01 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14806 | Slave01 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14807 | Slave01 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14808 | Slave01 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14809 | Slave01 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14810 | Slave01 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14811 | Slave01 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14812 | Slave01 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14813 | Slave01 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14814 | Slave01 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14815 | Slave01 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14816 | Slave01 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14817 | Slave01 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14818 | Slave01 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14819 | Slave01 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14820 | Slave01 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14821 | Slave01 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14822 | Slave01 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14823 | Slave01 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14824 | Slave01 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14825 | Slave01 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14826 | Slave01 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14827 | Slave01 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14828 | Slave01 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14829 | Slave01 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14830 | Slave01 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14831 | Slave01 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14832 | Slave01 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14833 | Slave01 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14834 | Slave01 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14835 | Slave01 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14836 | Slave01 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14837 | Slave01 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14838 | Slave01 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14839 | Slave01 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14840 | Slave01 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14841 | Slave01 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14842 | Slave01 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14843 | Slave01 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14844 | Slave01 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14845 | Slave01 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14846 | Slave01 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14847 | Slave01 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14848 | Slave02 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14849 | Slave02 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14850 | Slave02 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14851 | Slave02 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14852 | Slave02 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14853 | Slave02 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14854 | Slave02 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14855 | Slave02 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14856 | Slave02 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14857 | Slave02 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14858 | Slave02 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14859 | Slave02 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14860 | Slave02 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14861 | Slave02 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14862 | Slave02 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14863 | Slave02 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14864 | Slave02 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14865 | Slave02 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14866 | Slave02 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14867 | Slave02 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14868 | Slave02 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14869 | Slave02 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14870 | Slave02 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14871 | Slave02 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14872 | Slave02 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14873 | Slave02 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14874 | Slave02 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14875 | Slave02 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14876 | Slave02 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14877 | Slave02 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14878 | Slave02 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14879 | Slave02 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14880 | Slave02 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14881 | Slave02 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14882 | Slave02 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14883 | Slave02 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14884 | Slave02 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14885 | Slave02 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14886 | Slave02 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14887 | Slave02 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14888 | Slave02 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14889 | Slave02 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14890 | Slave02 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14891 | Slave02 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14892 | Slave02 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14893 | Slave02 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14894 | Slave02 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14895 | Slave02 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14896 | Slave03 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14897 | Slave03 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14898 | Slave03 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14899 | Slave03 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14900 | Slave03 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14901 | Slave03 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14902 | Slave03 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14903 | Slave03 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14904 | Slave03 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14905 | Slave03 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14906 | Slave03 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14907 | Slave03 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14908 | Slave03 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14909 | Slave03 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14910 | Slave03 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14911 | Slave03 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14912 | Slave03 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14913 | Slave03 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14914 | Slave03 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14915 | Slave03 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14916 | Slave03 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14917 | Slave03 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14918 | Slave03 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14919 | Slave03 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14920 | Slave03 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14921 | Slave03 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14922 | Slave03 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14923 | Slave03 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14924 | Slave03 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14925 | Slave03 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14926 | Slave03 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14927 | Slave03 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14928 | Slave03 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14929 | Slave03 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14930 | Slave03 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14931 | Slave03 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14932 | Slave03 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14933 | Slave03 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14934 | Slave03 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14935 | Slave03 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14936 | Slave03 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14937 | Slave03 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14938 | Slave03 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14939 | Slave03 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14940 | Slave03 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14941 | Slave03 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14942 | Slave03 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14943 | Slave03 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14944 | Slave04 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14945 | Slave04 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14946 | Slave04 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14947 | Slave04 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14948 | Slave04 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14949 | Slave04 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14950 | Slave04 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14951 | Slave04 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14952 | Slave04 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14953 | Slave04 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14954 | Slave04 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14955 | Slave04 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14956 | Slave04 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14957 | Slave04 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14958 | Slave04 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14959 | Slave04 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14960 | Slave04 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14961 | Slave04 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14962 | Slave04 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14963 | Slave04 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14964 | Slave04 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14965 | Slave04 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14966 | Slave04 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14967 | Slave04 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14968 | Slave04 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14969 | Slave04 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14970 | Slave04 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14971 | Slave04 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14972 | Slave04 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14973 | Slave04 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14974 | Slave04 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14975 | Slave04 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14976 | Slave04 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14977 | Slave04 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14978 | Slave04 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14979 | Slave04 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14980 | Slave04 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14981 | Slave04 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14982 | Slave04 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14983 | Slave04 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14984 | Slave04 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14985 | Slave04 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14986 | Slave04 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14987 | Slave04 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14988 | Slave04 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14989 | Slave04 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14990 | Slave04 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14991 | Slave04 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14992 | Slave05 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14993 | Slave05 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14994 | Slave05 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14995 | Slave05 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14996 | Slave05 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14997 | Slave05 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14998 | Slave05 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
14999 | Slave05 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15000 | Slave05 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15001 | Slave05 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15002 | Slave05 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15003 | Slave05 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15004 | Slave05 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15005 | Slave05 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15006 | Slave05 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15007 | Slave05 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15008 | Slave05 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15009 | Slave05 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15010 | Slave05 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15011 | Slave05 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15012 | Slave05 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15013 | Slave05 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15014 | Slave05 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15015 | Slave05 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15016 | Slave05 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15017 | Slave05 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15018 | Slave05 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15019 | Slave05 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15020 | Slave05 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15021 | Slave05 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15022 | Slave05 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15023 | Slave05 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15024 | Slave05 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15025 | Slave05 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15026 | Slave05 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15027 | Slave05 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15028 | Slave05 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15029 | Slave05 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15030 | Slave05 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15031 | Slave05 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15032 | Slave05 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15033 | Slave05 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15034 | Slave05 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15035 | Slave05 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15036 | Slave05 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15037 | Slave05 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15038 | Slave05 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15039 | Slave05 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15040 | Slave06 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15041 | Slave06 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15042 | Slave06 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15043 | Slave06 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15044 | Slave06 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15045 | Slave06 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15046 | Slave06 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15047 | Slave06 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15048 | Slave06 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15049 | Slave06 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15050 | Slave06 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15051 | Slave06 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15052 | Slave06 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15053 | Slave06 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15054 | Slave06 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15055 | Slave06 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15056 | Slave06 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15057 | Slave06 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15058 | Slave06 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15059 | Slave06 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15060 | Slave06 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15061 | Slave06 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15062 | Slave06 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15063 | Slave06 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15064 | Slave06 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15065 | Slave06 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15066 | Slave06 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15067 | Slave06 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15068 | Slave06 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15069 | Slave06 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15070 | Slave06 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15071 | Slave06 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15072 | Slave06 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15073 | Slave06 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15074 | Slave06 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15075 | Slave06 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15076 | Slave06 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15077 | Slave06 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15078 | Slave06 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15079 | Slave06 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15080 | Slave06 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15081 | Slave06 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15082 | Slave06 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15083 | Slave06 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15084 | Slave06 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15085 | Slave06 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15086 | Slave06 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15087 | Slave06 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15088 | Slave07 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15089 | Slave07 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15090 | Slave07 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15091 | Slave07 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15092 | Slave07 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15093 | Slave07 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15094 | Slave07 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15095 | Slave07 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15096 | Slave07 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15097 | Slave07 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15098 | Slave07 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15099 | Slave07 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15100 | Slave07 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15101 | Slave07 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15102 | Slave07 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15103 | Slave07 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15104 | Slave07 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15105 | Slave07 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15106 | Slave07 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15107 | Slave07 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15108 | Slave07 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15109 | Slave07 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15110 | Slave07 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15111 | Slave07 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15112 | Slave07 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15113 | Slave07 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15114 | Slave07 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15115 | Slave07 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15116 | Slave07 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15117 | Slave07 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15118 | Slave07 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15119 | Slave07 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15120 | Slave07 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15121 | Slave07 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15122 | Slave07 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15123 | Slave07 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15124 | Slave07 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15125 | Slave07 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15126 | Slave07 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15127 | Slave07 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15128 | Slave07 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15129 | Slave07 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15130 | Slave07 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15131 | Slave07 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15132 | Slave07 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15133 | Slave07 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15134 | Slave07 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15135 | Slave07 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15136 | Slave08 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15137 | Slave08 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15138 | Slave08 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15139 | Slave08 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15140 | Slave08 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15141 | Slave08 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15142 | Slave08 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15143 | Slave08 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15144 | Slave08 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15145 | Slave08 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15146 | Slave08 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15147 | Slave08 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15148 | Slave08 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15149 | Slave08 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15150 | Slave08 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15151 | Slave08 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15152 | Slave08 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15153 | Slave08 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15154 | Slave08 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15155 | Slave08 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15156 | Slave08 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15157 | Slave08 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15158 | Slave08 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15159 | Slave08 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15160 | Slave08 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15161 | Slave08 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15162 | Slave08 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15163 | Slave08 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15164 | Slave08 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15165 | Slave08 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15166 | Slave08 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15167 | Slave08 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15168 | Slave08 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15169 | Slave08 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15170 | Slave08 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15171 | Slave08 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15172 | Slave08 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15173 | Slave08 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15174 | Slave08 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15175 | Slave08 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15176 | Slave08 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15177 | Slave08 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15178 | Slave08 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15179 | Slave08 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15180 | Slave08 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15181 | Slave08 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15182 | Slave08 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15183 | Slave08 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15184 | Slave09 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15185 | Slave09 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15186 | Slave09 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15187 | Slave09 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15188 | Slave09 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15189 | Slave09 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15190 | Slave09 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15191 | Slave09 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15192 | Slave09 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15193 | Slave09 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15194 | Slave09 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15195 | Slave09 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15196 | Slave09 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15197 | Slave09 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15198 | Slave09 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15199 | Slave09 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15200 | Slave09 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15201 | Slave09 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15202 | Slave09 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15203 | Slave09 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15204 | Slave09 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15205 | Slave09 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15206 | Slave09 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15207 | Slave09 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15208 | Slave09 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15209 | Slave09 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15210 | Slave09 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15211 | Slave09 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15212 | Slave09 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15213 | Slave09 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15214 | Slave09 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15215 | Slave09 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15216 | Slave09 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15217 | Slave09 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15218 | Slave09 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15219 | Slave09 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15220 | Slave09 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15221 | Slave09 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15222 | Slave09 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15223 | Slave09 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15224 | Slave09 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15225 | Slave09 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15226 | Slave09 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15227 | Slave09 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15228 | Slave09 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15229 | Slave09 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15230 | Slave09 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15231 | Slave09 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15232 | Slave10 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15233 | Slave10 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15234 | Slave10 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15235 | Slave10 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15236 | Slave10 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15237 | Slave10 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15238 | Slave10 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15239 | Slave10 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15240 | Slave10 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15241 | Slave10 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15242 | Slave10 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15243 | Slave10 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15244 | Slave10 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15245 | Slave10 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15246 | Slave10 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15247 | Slave10 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15248 | Slave10 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15249 | Slave10 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15250 | Slave10 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15251 | Slave10 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15252 | Slave10 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15253 | Slave10 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15254 | Slave10 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15255 | Slave10 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15256 | Slave10 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15257 | Slave10 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15258 | Slave10 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15259 | Slave10 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15260 | Slave10 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15261 | Slave10 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15262 | Slave10 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15263 | Slave10 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15264 | Slave10 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15265 | Slave10 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15266 | Slave10 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15267 | Slave10 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15268 | Slave10 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15269 | Slave10 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15270 | Slave10 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15271 | Slave10 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15272 | Slave10 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15273 | Slave10 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15274 | Slave10 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15275 | Slave10 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15276 | Slave10 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15277 | Slave10 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15278 | Slave10 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15279 | Slave10 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15280 | Slave11 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15281 | Slave11 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15282 | Slave11 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15283 | Slave11 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15284 | Slave11 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15285 | Slave11 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15286 | Slave11 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15287 | Slave11 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15288 | Slave11 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15289 | Slave11 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15290 | Slave11 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15291 | Slave11 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15292 | Slave11 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15293 | Slave11 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15294 | Slave11 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15295 | Slave11 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15296 | Slave11 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15297 | Slave11 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15298 | Slave11 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15299 | Slave11 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15300 | Slave11 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15301 | Slave11 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15302 | Slave11 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15303 | Slave11 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15304 | Slave11 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15305 | Slave11 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15306 | Slave11 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15307 | Slave11 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15308 | Slave11 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15309 | Slave11 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15310 | Slave11 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15311 | Slave11 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15312 | Slave11 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15313 | Slave11 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15314 | Slave11 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15315 | Slave11 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15316 | Slave11 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15317 | Slave11 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15318 | Slave11 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15319 | Slave11 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15320 | Slave11 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15321 | Slave11 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15322 | Slave11 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15323 | Slave11 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15324 | Slave11 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15325 | Slave11 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15326 | Slave11 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15327 | Slave11 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15328 | Slave12 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15329 | Slave12 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15330 | Slave12 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15331 | Slave12 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15332 | Slave12 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15333 | Slave12 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15334 | Slave12 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15335 | Slave12 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15336 | Slave12 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15337 | Slave12 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15338 | Slave12 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15339 | Slave12 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15340 | Slave12 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15341 | Slave12 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15342 | Slave12 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15343 | Slave12 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15344 | Slave12 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15345 | Slave12 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15346 | Slave12 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15347 | Slave12 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15348 | Slave12 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15349 | Slave12 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15350 | Slave12 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15351 | Slave12 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15352 | Slave12 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15353 | Slave12 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15354 | Slave12 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15355 | Slave12 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15356 | Slave12 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15357 | Slave12 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15358 | Slave12 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15359 | Slave12 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15360 | Slave12 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15361 | Slave12 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15362 | Slave12 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15363 | Slave12 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15364 | Slave12 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15365 | Slave12 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15366 | Slave12 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15367 | Slave12 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15368 | Slave12 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15369 | Slave12 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15370 | Slave12 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15371 | Slave12 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15372 | Slave12 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15373 | Slave12 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15374 | Slave12 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15375 | Slave12 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15376 | Slave13 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15377 | Slave13 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15378 | Slave13 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15379 | Slave13 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15380 | Slave13 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15381 | Slave13 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15382 | Slave13 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15383 | Slave13 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15384 | Slave13 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15385 | Slave13 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15386 | Slave13 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15387 | Slave13 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15388 | Slave13 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15389 | Slave13 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15390 | Slave13 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15391 | Slave13 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15392 | Slave13 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15393 | Slave13 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15394 | Slave13 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15395 | Slave13 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15396 | Slave13 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15397 | Slave13 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15398 | Slave13 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15399 | Slave13 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15400 | Slave13 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15401 | Slave13 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15402 | Slave13 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15403 | Slave13 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15404 | Slave13 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15405 | Slave13 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15406 | Slave13 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15407 | Slave13 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15408 | Slave13 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15409 | Slave13 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15410 | Slave13 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15411 | Slave13 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15412 | Slave13 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15413 | Slave13 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15414 | Slave13 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15415 | Slave13 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15416 | Slave13 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15417 | Slave13 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15418 | Slave13 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15419 | Slave13 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15420 | Slave13 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15421 | Slave13 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15422 | Slave13 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15423 | Slave13 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15424 | Slave14 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15425 | Slave14 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15426 | Slave14 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15427 | Slave14 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15428 | Slave14 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15429 | Slave14 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15430 | Slave14 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15431 | Slave14 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15432 | Slave14 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15433 | Slave14 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15434 | Slave14 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15435 | Slave14 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15436 | Slave14 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15437 | Slave14 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15438 | Slave14 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15439 | Slave14 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15440 | Slave14 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15441 | Slave14 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15442 | Slave14 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15443 | Slave14 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15444 | Slave14 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15445 | Slave14 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15446 | Slave14 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15447 | Slave14 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15448 | Slave14 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15449 | Slave14 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15450 | Slave14 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15451 | Slave14 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15452 | Slave14 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15453 | Slave14 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15454 | Slave14 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15455 | Slave14 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15456 | Slave14 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15457 | Slave14 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15458 | Slave14 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15459 | Slave14 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15460 | Slave14 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15461 | Slave14 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15462 | Slave14 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15463 | Slave14 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15464 | Slave14 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15465 | Slave14 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15466 | Slave14 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15467 | Slave14 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15468 | Slave14 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15469 | Slave14 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15470 | Slave14 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15471 | Slave14 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15472 | Slave15 Outlet Port01 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15473 | Slave15 Outlet Port02 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15474 | Slave15 Outlet Port03 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15475 | Slave15 Outlet Port04 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15476 | Slave15 Outlet Port05 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15477 | Slave15 Outlet Port06 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15478 | Slave15 Outlet Port07 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15479 | Slave15 Outlet Port08 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15480 | Slave15 Outlet Port09 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15481 | Slave15 Outlet Port10 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15482 | Slave15 Outlet Port11 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15483 | Slave15 Outlet Port12 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15484 | Slave15 Outlet Port13 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15485 | Slave15 Outlet Port14 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15486 | Slave15 Outlet Port15 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15487 | Slave15 Outlet Port16 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15488 | Slave15 Outlet Port17 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15489 | Slave15 Outlet Port18 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15490 | Slave15 Outlet Port19 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15491 | Slave15 Outlet Port20 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15492 | Slave15 Outlet Port21 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15493 | Slave15 Outlet Port22 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15494 | Slave15 Outlet Port23 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15495 | Slave15 Outlet Port24 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15496 | Slave15 Outlet Port25 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15497 | Slave15 Outlet Port26 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15498 | Slave15 Outlet Port27 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15499 | Slave15 Outlet Port28 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15500 | Slave15 Outlet Port29 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15501 | Slave15 Outlet Port30 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15502 | Slave15 Outlet Port31 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15503 | Slave15 Outlet Port32 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15504 | Slave15 Outlet Port33 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15505 | Slave15 Outlet Port34 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15506 | Slave15 Outlet Port35 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15507 | Slave15 Outlet Port36 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15508 | Slave15 Outlet Port37 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15509 | Slave15 Outlet Port38 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15510 | Slave15 Outlet Port39 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15511 | Slave15 Outlet Port40 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15512 | Slave15 Outlet Port41 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15513 | Slave15 Outlet Port42 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15514 | Slave15 Outlet Port43 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15515 | Slave15 Outlet Port44 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15516 | Slave15 Outlet Port45 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15517 | Slave15 Outlet Port46 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15518 | Slave15 Outlet Port47 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15519 | Slave15 Outlet Port48 Reboot Time | RW | 2 bytes | Range is 5 ~ 60
15520 | Master Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15521 | Master Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15522 | Master Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15523 | Master Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15524 | Master Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15525 | Master Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15526 | Master Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15527 | Master Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15528 | Master Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15529 | Master Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15530 | Master Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15531 | Master Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15532 | Master Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15533 | Master Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15534 | Master Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15535 | Master Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15536 | Master Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15537 | Master Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15538 | Master Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15539 | Master Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15540 | Master Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15541 | Master Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15542 | Master Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15543 | Master Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15544 | Master Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15545 | Master Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15546 | Master Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15547 | Master Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15548 | Master Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15549 | Master Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15550 | Master Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15551 | Master Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15552 | Master Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15553 | Master Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15554 | Master Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15555 | Master Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15556 | Master Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15557 | Master Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15558 | Master Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15559 | Master Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15560 | Master Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15561 | Master Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15562 | Master Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15563 | Master Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15564 | Master Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15565 | Master Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15566 | Master Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15567 | Master Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15568 | Slave01 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15569 | Slave01 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15570 | Slave01 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15571 | Slave01 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15572 | Slave01 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15573 | Slave01 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15574 | Slave01 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15575 | Slave01 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15576 | Slave01 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15577 | Slave01 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15578 | Slave01 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15579 | Slave01 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15580 | Slave01 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15581 | Slave01 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15582 | Slave01 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15583 | Slave01 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15584 | Slave01 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15585 | Slave01 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15586 | Slave01 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15587 | Slave01 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15588 | Slave01 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15589 | Slave01 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15590 | Slave01 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15591 | Slave01 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15592 | Slave01 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15593 | Slave01 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15594 | Slave01 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15595 | Slave01 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15596 | Slave01 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15597 | Slave01 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15598 | Slave01 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15599 | Slave01 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15600 | Slave01 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15601 | Slave01 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15602 | Slave01 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15603 | Slave01 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15604 | Slave01 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15605 | Slave01 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15606 | Slave01 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15607 | Slave01 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15608 | Slave01 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15609 | Slave01 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15610 | Slave01 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15611 | Slave01 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15612 | Slave01 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15613 | Slave01 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15614 | Slave01 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15615 | Slave01 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15616 | Slave02 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15617 | Slave02 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15618 | Slave02 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15619 | Slave02 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15620 | Slave02 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15621 | Slave02 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15622 | Slave02 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15623 | Slave02 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15624 | Slave02 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15625 | Slave02 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15626 | Slave02 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15627 | Slave02 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15628 | Slave02 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15629 | Slave02 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15630 | Slave02 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15631 | Slave02 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15632 | Slave02 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15633 | Slave02 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15634 | Slave02 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15635 | Slave02 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15636 | Slave02 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15637 | Slave02 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15638 | Slave02 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15639 | Slave02 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15640 | Slave02 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15641 | Slave02 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15642 | Slave02 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15643 | Slave02 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15644 | Slave02 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15645 | Slave02 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15646 | Slave02 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15647 | Slave02 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15648 | Slave02 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15649 | Slave02 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15650 | Slave02 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15651 | Slave02 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15652 | Slave02 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15653 | Slave02 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15654 | Slave02 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15655 | Slave02 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15656 | Slave02 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15657 | Slave02 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15658 | Slave02 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15659 | Slave02 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15660 | Slave02 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15661 | Slave02 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15662 | Slave02 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15663 | Slave02 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15664 | Slave03 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15665 | Slave03 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15666 | Slave03 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15667 | Slave03 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15668 | Slave03 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15669 | Slave03 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15670 | Slave03 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15671 | Slave03 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15672 | Slave03 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15673 | Slave03 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15674 | Slave03 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15675 | Slave03 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15676 | Slave03 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15677 | Slave03 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15678 | Slave03 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15679 | Slave03 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15680 | Slave03 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15681 | Slave03 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15682 | Slave03 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15683 | Slave03 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15684 | Slave03 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15685 | Slave03 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15686 | Slave03 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15687 | Slave03 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15688 | Slave03 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15689 | Slave03 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15690 | Slave03 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15691 | Slave03 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15692 | Slave03 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15693 | Slave03 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15694 | Slave03 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15695 | Slave03 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15696 | Slave03 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15697 | Slave03 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15698 | Slave03 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15699 | Slave03 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15700 | Slave03 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15701 | Slave03 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15702 | Slave03 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15703 | Slave03 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15704 | Slave03 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15705 | Slave03 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15706 | Slave03 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15707 | Slave03 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15708 | Slave03 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15709 | Slave03 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15710 | Slave03 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15711 | Slave03 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15712 | Slave04 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15713 | Slave04 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15714 | Slave04 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15715 | Slave04 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15716 | Slave04 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15717 | Slave04 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15718 | Slave04 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15719 | Slave04 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15720 | Slave04 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15721 | Slave04 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15722 | Slave04 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15723 | Slave04 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15724 | Slave04 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15725 | Slave04 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15726 | Slave04 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15727 | Slave04 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15728 | Slave04 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15729 | Slave04 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15730 | Slave04 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15731 | Slave04 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15732 | Slave04 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15733 | Slave04 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15734 | Slave04 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15735 | Slave04 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15736 | Slave04 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15737 | Slave04 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15738 | Slave04 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15739 | Slave04 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15740 | Slave04 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15741 | Slave04 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15742 | Slave04 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15743 | Slave04 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15744 | Slave04 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15745 | Slave04 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15746 | Slave04 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15747 | Slave04 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15748 | Slave04 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15749 | Slave04 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15750 | Slave04 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15751 | Slave04 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15752 | Slave04 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15753 | Slave04 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15754 | Slave04 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15755 | Slave04 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15756 | Slave04 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15757 | Slave04 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15758 | Slave04 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15759 | Slave04 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15760 | Slave05 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15761 | Slave05 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15762 | Slave05 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15763 | Slave05 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15764 | Slave05 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15765 | Slave05 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15766 | Slave05 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15767 | Slave05 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15768 | Slave05 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15769 | Slave05 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15770 | Slave05 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15771 | Slave05 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15772 | Slave05 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15773 | Slave05 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15774 | Slave05 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15775 | Slave05 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15776 | Slave05 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15777 | Slave05 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15778 | Slave05 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15779 | Slave05 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15780 | Slave05 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15781 | Slave05 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15782 | Slave05 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15783 | Slave05 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15784 | Slave05 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15785 | Slave05 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15786 | Slave05 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15787 | Slave05 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15788 | Slave05 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15789 | Slave05 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15790 | Slave05 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15791 | Slave05 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15792 | Slave05 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15793 | Slave05 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15794 | Slave05 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15795 | Slave05 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15796 | Slave05 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15797 | Slave05 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15798 | Slave05 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15799 | Slave05 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15800 | Slave05 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15801 | Slave05 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15802 | Slave05 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15803 | Slave05 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15804 | Slave05 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15805 | Slave05 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15806 | Slave05 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15807 | Slave05 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15808 | Slave06 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15809 | Slave06 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15810 | Slave06 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15811 | Slave06 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15812 | Slave06 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15813 | Slave06 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15814 | Slave06 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15815 | Slave06 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15816 | Slave06 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15817 | Slave06 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15818 | Slave06 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15819 | Slave06 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15820 | Slave06 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15821 | Slave06 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15822 | Slave06 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15823 | Slave06 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15824 | Slave06 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15825 | Slave06 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15826 | Slave06 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15827 | Slave06 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15828 | Slave06 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15829 | Slave06 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15830 | Slave06 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15831 | Slave06 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15832 | Slave06 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15833 | Slave06 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15834 | Slave06 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15835 | Slave06 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15836 | Slave06 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15837 | Slave06 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15838 | Slave06 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15839 | Slave06 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15840 | Slave06 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15841 | Slave06 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15842 | Slave06 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15843 | Slave06 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15844 | Slave06 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15845 | Slave06 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15846 | Slave06 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15847 | Slave06 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15848 | Slave06 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15849 | Slave06 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15850 | Slave06 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15851 | Slave06 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15852 | Slave06 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15853 | Slave06 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15854 | Slave06 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15855 | Slave06 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15856 | Slave07 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15857 | Slave07 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15858 | Slave07 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15859 | Slave07 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15860 | Slave07 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15861 | Slave07 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15862 | Slave07 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15863 | Slave07 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15864 | Slave07 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15865 | Slave07 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15866 | Slave07 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15867 | Slave07 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15868 | Slave07 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15869 | Slave07 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15870 | Slave07 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15871 | Slave07 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15872 | Slave07 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15873 | Slave07 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15874 | Slave07 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15875 | Slave07 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15876 | Slave07 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15877 | Slave07 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15878 | Slave07 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15879 | Slave07 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15880 | Slave07 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15881 | Slave07 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15882 | Slave07 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15883 | Slave07 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15884 | Slave07 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15885 | Slave07 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15886 | Slave07 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15887 | Slave07 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15888 | Slave07 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15889 | Slave07 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15890 | Slave07 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15891 | Slave07 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15892 | Slave07 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15893 | Slave07 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15894 | Slave07 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15895 | Slave07 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15896 | Slave07 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15897 | Slave07 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15898 | Slave07 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15899 | Slave07 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15900 | Slave07 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15901 | Slave07 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15902 | Slave07 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15903 | Slave07 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15904 | Slave08 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15905 | Slave08 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15906 | Slave08 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15907 | Slave08 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15908 | Slave08 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15909 | Slave08 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15910 | Slave08 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15911 | Slave08 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15912 | Slave08 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15913 | Slave08 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15914 | Slave08 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15915 | Slave08 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15916 | Slave08 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15917 | Slave08 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15918 | Slave08 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15919 | Slave08 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15920 | Slave08 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15921 | Slave08 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15922 | Slave08 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15923 | Slave08 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15924 | Slave08 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15925 | Slave08 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15926 | Slave08 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15927 | Slave08 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15928 | Slave08 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15929 | Slave08 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15930 | Slave08 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15931 | Slave08 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15932 | Slave08 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15933 | Slave08 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15934 | Slave08 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15935 | Slave08 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15936 | Slave08 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15937 | Slave08 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15938 | Slave08 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15939 | Slave08 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15940 | Slave08 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15941 | Slave08 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15942 | Slave08 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15943 | Slave08 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15944 | Slave08 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15945 | Slave08 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15946 | Slave08 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15947 | Slave08 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15948 | Slave08 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15949 | Slave08 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15950 | Slave08 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15951 | Slave08 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15952 | Slave09 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15953 | Slave09 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15954 | Slave09 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15955 | Slave09 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15956 | Slave09 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15957 | Slave09 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15958 | Slave09 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15959 | Slave09 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15960 | Slave09 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15961 | Slave09 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15962 | Slave09 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15963 | Slave09 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15964 | Slave09 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15965 | Slave09 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15966 | Slave09 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15967 | Slave09 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15968 | Slave09 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15969 | Slave09 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15970 | Slave09 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15971 | Slave09 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15972 | Slave09 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15973 | Slave09 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15974 | Slave09 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15975 | Slave09 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15976 | Slave09 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15977 | Slave09 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15978 | Slave09 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15979 | Slave09 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15980 | Slave09 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15981 | Slave09 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15982 | Slave09 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15983 | Slave09 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15984 | Slave09 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15985 | Slave09 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15986 | Slave09 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15987 | Slave09 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15988 | Slave09 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15989 | Slave09 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15990 | Slave09 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15991 | Slave09 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15992 | Slave09 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15993 | Slave09 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15994 | Slave09 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15995 | Slave09 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15996 | Slave09 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15997 | Slave09 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15998 | Slave09 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
15999 | Slave09 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16000 | Slave10 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16001 | Slave10 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16002 | Slave10 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16003 | Slave10 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16004 | Slave10 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16005 | Slave10 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16006 | Slave10 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16007 | Slave10 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16008 | Slave10 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16009 | Slave10 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16010 | Slave10 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16011 | Slave10 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16012 | Slave10 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16013 | Slave10 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16014 | Slave10 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16015 | Slave10 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16016 | Slave10 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16017 | Slave10 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16018 | Slave10 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16019 | Slave10 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16020 | Slave10 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16021 | Slave10 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16022 | Slave10 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16023 | Slave10 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16024 | Slave10 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16025 | Slave10 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16026 | Slave10 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16027 | Slave10 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16028 | Slave10 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16029 | Slave10 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16030 | Slave10 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16031 | Slave10 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16032 | Slave10 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16033 | Slave10 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16034 | Slave10 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16035 | Slave10 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16036 | Slave10 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16037 | Slave10 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16038 | Slave10 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16039 | Slave10 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16040 | Slave10 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16041 | Slave10 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16042 | Slave10 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16043 | Slave10 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16044 | Slave10 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16045 | Slave10 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16046 | Slave10 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16047 | Slave10 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16048 | Slave11 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16049 | Slave11 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16050 | Slave11 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16051 | Slave11 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16052 | Slave11 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16053 | Slave11 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16054 | Slave11 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16055 | Slave11 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16056 | Slave11 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16057 | Slave11 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16058 | Slave11 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16059 | Slave11 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16060 | Slave11 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16061 | Slave11 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16062 | Slave11 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16063 | Slave11 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16064 | Slave11 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16065 | Slave11 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16066 | Slave11 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16067 | Slave11 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16068 | Slave11 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16069 | Slave11 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16070 | Slave11 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16071 | Slave11 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16072 | Slave11 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16073 | Slave11 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16074 | Slave11 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16075 | Slave11 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16076 | Slave11 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16077 | Slave11 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16078 | Slave11 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16079 | Slave11 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16080 | Slave11 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16081 | Slave11 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16082 | Slave11 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16083 | Slave11 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16084 | Slave11 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16085 | Slave11 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16086 | Slave11 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16087 | Slave11 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16088 | Slave11 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16089 | Slave11 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16090 | Slave11 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16091 | Slave11 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16092 | Slave11 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16093 | Slave11 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16094 | Slave11 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16095 | Slave11 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16096 | Slave12 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16097 | Slave12 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16098 | Slave12 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16099 | Slave12 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16100 | Slave12 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16101 | Slave12 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16102 | Slave12 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16103 | Slave12 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16104 | Slave12 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16105 | Slave12 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16106 | Slave12 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16107 | Slave12 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16108 | Slave12 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16109 | Slave12 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16110 | Slave12 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16111 | Slave12 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16112 | Slave12 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16113 | Slave12 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16114 | Slave12 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16115 | Slave12 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16116 | Slave12 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16117 | Slave12 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16118 | Slave12 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16119 | Slave12 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16120 | Slave12 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16121 | Slave12 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16122 | Slave12 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16123 | Slave12 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16124 | Slave12 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16125 | Slave12 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16126 | Slave12 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16127 | Slave12 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16128 | Slave12 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16129 | Slave12 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16130 | Slave12 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16131 | Slave12 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16132 | Slave12 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16133 | Slave12 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16134 | Slave12 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16135 | Slave12 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16136 | Slave12 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16137 | Slave12 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16138 | Slave12 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16139 | Slave12 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16140 | Slave12 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16141 | Slave12 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16142 | Slave12 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16143 | Slave12 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16144 | Slave13 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16145 | Slave13 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16146 | Slave13 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16147 | Slave13 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16148 | Slave13 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16149 | Slave13 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16150 | Slave13 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16151 | Slave13 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16152 | Slave13 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16153 | Slave13 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16154 | Slave13 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16155 | Slave13 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16156 | Slave13 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16157 | Slave13 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16158 | Slave13 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16159 | Slave13 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16160 | Slave13 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16161 | Slave13 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16162 | Slave13 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16163 | Slave13 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16164 | Slave13 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16165 | Slave13 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16166 | Slave13 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16167 | Slave13 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16168 | Slave13 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16169 | Slave13 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16170 | Slave13 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16171 | Slave13 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16172 | Slave13 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16173 | Slave13 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16174 | Slave13 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16175 | Slave13 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16176 | Slave13 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16177 | Slave13 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16178 | Slave13 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16179 | Slave13 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16180 | Slave13 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16181 | Slave13 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16182 | Slave13 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16183 | Slave13 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16184 | Slave13 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16185 | Slave13 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16186 | Slave13 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16187 | Slave13 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16188 | Slave13 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16189 | Slave13 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16190 | Slave13 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16191 | Slave13 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16192 | Slave14 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16193 | Slave14 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16194 | Slave14 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16195 | Slave14 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16196 | Slave14 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16197 | Slave14 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16198 | Slave14 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16199 | Slave14 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16200 | Slave14 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16201 | Slave14 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16202 | Slave14 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16203 | Slave14 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16204 | Slave14 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16205 | Slave14 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16206 | Slave14 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16207 | Slave14 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16208 | Slave14 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16209 | Slave14 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16210 | Slave14 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16211 | Slave14 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16212 | Slave14 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16213 | Slave14 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16214 | Slave14 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16215 | Slave14 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16216 | Slave14 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16217 | Slave14 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16218 | Slave14 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16219 | Slave14 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16220 | Slave14 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16221 | Slave14 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16222 | Slave14 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16223 | Slave14 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16224 | Slave14 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16225 | Slave14 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16226 | Slave14 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16227 | Slave14 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16228 | Slave14 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16229 | Slave14 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16230 | Slave14 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16231 | Slave14 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16232 | Slave14 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16233 | Slave14 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16234 | Slave14 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16235 | Slave14 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16236 | Slave14 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16237 | Slave14 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16238 | Slave14 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16239 | Slave14 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16240 | Slave15 Outlet Port01 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16241 | Slave15 Outlet Port02 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16242 | Slave15 Outlet Port03 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16243 | Slave15 Outlet Port04 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16244 | Slave15 Outlet Port05 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16245 | Slave15 Outlet Port06 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16246 | Slave15 Outlet Port07 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16247 | Slave15 Outlet Port08 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16248 | Slave15 Outlet Port09 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16249 | Slave15 Outlet Port10 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16250 | Slave15 Outlet Port11 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16251 | Slave15 Outlet Port12 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16252 | Slave15 Outlet Port13 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16253 | Slave15 Outlet Port14 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16254 | Slave15 Outlet Port15 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16255 | Slave15 Outlet Port16 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16256 | Slave15 Outlet Port17 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16257 | Slave15 Outlet Port18 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16258 | Slave15 Outlet Port19 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16259 | Slave15 Outlet Port20 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16260 | Slave15 Outlet Port21 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16261 | Slave15 Outlet Port22 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16262 | Slave15 Outlet Port23 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16263 | Slave15 Outlet Port24 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16264 | Slave15 Outlet Port25 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16265 | Slave15 Outlet Port26 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16266 | Slave15 Outlet Port27 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16267 | Slave15 Outlet Port28 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16268 | Slave15 Outlet Port29 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16269 | Slave15 Outlet Port30 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16270 | Slave15 Outlet Port31 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16271 | Slave15 Outlet Port32 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16272 | Slave15 Outlet Port33 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16273 | Slave15 Outlet Port34 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16274 | Slave15 Outlet Port35 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16275 | Slave15 Outlet Port36 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16276 | Slave15 Outlet Port37 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16277 | Slave15 Outlet Port38 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16278 | Slave15 Outlet Port39 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16279 | Slave15 Outlet Port40 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16280 | Slave15 Outlet Port41 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16281 | Slave15 Outlet Port42 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16282 | Slave15 Outlet Port43 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16283 | Slave15 Outlet Port44 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16284 | Slave15 Outlet Port45 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16285 | Slave15 Outlet Port46 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16286 | Slave15 Outlet Port47 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16287 | Slave15 Outlet Port48 Over Currrnt Warning | RW | 2 bytes | Unit:0.01A
16288 | Master Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16289 | Master Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16290 | Master Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16291 | Master Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16292 | Master Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16293 | Master Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16294 | Master Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16295 | Master Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16296 | Master Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16297 | Master Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16298 | Master Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16299 | Master Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16300 | Master Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16301 | Master Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16302 | Master Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16303 | Master Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16304 | Master Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16305 | Master Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16306 | Master Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16307 | Master Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16308 | Master Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16309 | Master Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16310 | Master Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16311 | Master Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16312 | Master Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16313 | Master Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16314 | Master Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16315 | Master Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16316 | Master Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16317 | Master Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16318 | Master Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16319 | Master Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16320 | Master Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16321 | Master Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16322 | Master Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16323 | Master Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16324 | Master Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16325 | Master Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16326 | Master Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16327 | Master Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16328 | Master Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16329 | Master Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16330 | Master Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16331 | Master Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16332 | Master Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16333 | Master Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16334 | Master Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16335 | Master Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16336 | Slave01 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16337 | Slave01 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16338 | Slave01 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16339 | Slave01 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16340 | Slave01 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16341 | Slave01 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16342 | Slave01 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16343 | Slave01 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16344 | Slave01 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16345 | Slave01 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16346 | Slave01 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16347 | Slave01 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16348 | Slave01 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16349 | Slave01 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16350 | Slave01 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16351 | Slave01 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16352 | Slave01 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16353 | Slave01 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16354 | Slave01 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16355 | Slave01 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16356 | Slave01 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16357 | Slave01 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16358 | Slave01 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16359 | Slave01 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16360 | Slave01 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16361 | Slave01 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16362 | Slave01 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16363 | Slave01 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16364 | Slave01 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16365 | Slave01 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16366 | Slave01 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16367 | Slave01 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16368 | Slave01 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16369 | Slave01 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16370 | Slave01 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16371 | Slave01 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16372 | Slave01 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16373 | Slave01 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16374 | Slave01 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16375 | Slave01 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16376 | Slave01 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16377 | Slave01 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16378 | Slave01 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16379 | Slave01 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16380 | Slave01 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16381 | Slave01 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16382 | Slave01 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16383 | Slave01 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16384 | Slave02 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16385 | Slave02 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16386 | Slave02 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16387 | Slave02 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16388 | Slave02 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16389 | Slave02 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16390 | Slave02 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16391 | Slave02 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16392 | Slave02 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16393 | Slave02 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16394 | Slave02 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16395 | Slave02 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16396 | Slave02 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16397 | Slave02 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16398 | Slave02 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16399 | Slave02 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16400 | Slave02 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16401 | Slave02 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16402 | Slave02 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16403 | Slave02 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16404 | Slave02 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16405 | Slave02 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16406 | Slave02 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16407 | Slave02 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16408 | Slave02 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16409 | Slave02 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16410 | Slave02 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16411 | Slave02 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16412 | Slave02 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16413 | Slave02 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16414 | Slave02 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16415 | Slave02 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16416 | Slave02 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16417 | Slave02 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16418 | Slave02 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16419 | Slave02 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16420 | Slave02 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16421 | Slave02 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16422 | Slave02 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16423 | Slave02 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16424 | Slave02 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16425 | Slave02 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16426 | Slave02 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16427 | Slave02 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16428 | Slave02 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16429 | Slave02 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16430 | Slave02 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16431 | Slave02 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16432 | Slave03 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16433 | Slave03 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16434 | Slave03 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16435 | Slave03 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16436 | Slave03 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16437 | Slave03 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16438 | Slave03 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16439 | Slave03 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16440 | Slave03 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16441 | Slave03 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16442 | Slave03 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16443 | Slave03 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16444 | Slave03 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16445 | Slave03 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16446 | Slave03 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16447 | Slave03 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16448 | Slave03 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16449 | Slave03 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16450 | Slave03 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16451 | Slave03 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16452 | Slave03 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16453 | Slave03 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16454 | Slave03 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16455 | Slave03 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16456 | Slave03 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16457 | Slave03 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16458 | Slave03 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16459 | Slave03 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16460 | Slave03 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16461 | Slave03 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16462 | Slave03 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16463 | Slave03 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16464 | Slave03 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16465 | Slave03 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16466 | Slave03 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16467 | Slave03 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16468 | Slave03 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16469 | Slave03 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16470 | Slave03 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16471 | Slave03 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16472 | Slave03 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16473 | Slave03 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16474 | Slave03 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16475 | Slave03 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16476 | Slave03 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16477 | Slave03 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16478 | Slave03 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16479 | Slave03 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16480 | Slave04 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16481 | Slave04 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16482 | Slave04 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16483 | Slave04 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16484 | Slave04 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16485 | Slave04 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16486 | Slave04 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16487 | Slave04 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16488 | Slave04 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16489 | Slave04 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16490 | Slave04 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16491 | Slave04 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16492 | Slave04 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16493 | Slave04 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16494 | Slave04 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16495 | Slave04 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16496 | Slave04 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16497 | Slave04 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16498 | Slave04 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16499 | Slave04 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16500 | Slave04 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16501 | Slave04 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16502 | Slave04 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16503 | Slave04 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16504 | Slave04 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16505 | Slave04 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16506 | Slave04 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16507 | Slave04 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16508 | Slave04 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16509 | Slave04 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16510 | Slave04 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16511 | Slave04 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16512 | Slave04 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16513 | Slave04 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16514 | Slave04 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16515 | Slave04 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16516 | Slave04 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16517 | Slave04 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16518 | Slave04 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16519 | Slave04 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16520 | Slave04 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16521 | Slave04 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16522 | Slave04 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16523 | Slave04 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16524 | Slave04 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16525 | Slave04 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16526 | Slave04 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16527 | Slave04 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16528 | Slave05 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16529 | Slave05 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16530 | Slave05 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16531 | Slave05 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16532 | Slave05 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16533 | Slave05 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16534 | Slave05 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16535 | Slave05 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16536 | Slave05 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16537 | Slave05 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16538 | Slave05 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16539 | Slave05 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16540 | Slave05 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16541 | Slave05 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16542 | Slave05 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16543 | Slave05 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16544 | Slave05 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16545 | Slave05 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16546 | Slave05 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16547 | Slave05 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16548 | Slave05 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16549 | Slave05 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16550 | Slave05 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16551 | Slave05 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16552 | Slave05 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16553 | Slave05 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16554 | Slave05 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16555 | Slave05 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16556 | Slave05 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16557 | Slave05 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16558 | Slave05 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16559 | Slave05 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16560 | Slave05 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16561 | Slave05 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16562 | Slave05 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16563 | Slave05 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16564 | Slave05 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16565 | Slave05 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16566 | Slave05 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16567 | Slave05 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16568 | Slave05 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16569 | Slave05 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16570 | Slave05 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16571 | Slave05 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16572 | Slave05 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16573 | Slave05 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16574 | Slave05 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16575 | Slave05 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16576 | Slave06 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16577 | Slave06 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16578 | Slave06 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16579 | Slave06 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16580 | Slave06 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16581 | Slave06 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16582 | Slave06 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16583 | Slave06 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16584 | Slave06 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16585 | Slave06 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16586 | Slave06 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16587 | Slave06 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16588 | Slave06 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16589 | Slave06 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16590 | Slave06 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16591 | Slave06 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16592 | Slave06 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16593 | Slave06 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16594 | Slave06 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16595 | Slave06 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16596 | Slave06 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16597 | Slave06 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16598 | Slave06 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16599 | Slave06 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16600 | Slave06 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16601 | Slave06 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16602 | Slave06 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16603 | Slave06 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16604 | Slave06 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16605 | Slave06 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16606 | Slave06 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16607 | Slave06 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16608 | Slave06 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16609 | Slave06 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16610 | Slave06 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16611 | Slave06 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16612 | Slave06 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16613 | Slave06 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16614 | Slave06 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16615 | Slave06 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16616 | Slave06 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16617 | Slave06 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16618 | Slave06 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16619 | Slave06 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16620 | Slave06 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16621 | Slave06 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16622 | Slave06 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16623 | Slave06 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16624 | Slave07 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16625 | Slave07 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16626 | Slave07 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16627 | Slave07 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16628 | Slave07 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16629 | Slave07 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16630 | Slave07 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16631 | Slave07 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16632 | Slave07 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16633 | Slave07 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16634 | Slave07 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16635 | Slave07 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16636 | Slave07 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16637 | Slave07 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16638 | Slave07 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16639 | Slave07 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16640 | Slave07 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16641 | Slave07 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16642 | Slave07 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16643 | Slave07 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16644 | Slave07 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16645 | Slave07 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16646 | Slave07 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16647 | Slave07 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16648 | Slave07 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16649 | Slave07 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16650 | Slave07 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16651 | Slave07 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16652 | Slave07 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16653 | Slave07 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16654 | Slave07 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16655 | Slave07 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16656 | Slave07 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16657 | Slave07 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16658 | Slave07 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16659 | Slave07 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16660 | Slave07 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16661 | Slave07 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16662 | Slave07 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16663 | Slave07 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16664 | Slave07 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16665 | Slave07 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16666 | Slave07 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16667 | Slave07 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16668 | Slave07 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16669 | Slave07 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16670 | Slave07 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16671 | Slave07 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16672 | Slave08 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16673 | Slave08 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16674 | Slave08 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16675 | Slave08 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16676 | Slave08 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16677 | Slave08 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16678 | Slave08 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16679 | Slave08 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16680 | Slave08 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16681 | Slave08 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16682 | Slave08 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16683 | Slave08 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16684 | Slave08 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16685 | Slave08 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16686 | Slave08 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16687 | Slave08 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16688 | Slave08 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16689 | Slave08 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16690 | Slave08 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16691 | Slave08 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16692 | Slave08 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16693 | Slave08 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16694 | Slave08 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16695 | Slave08 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16696 | Slave08 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16697 | Slave08 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16698 | Slave08 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16699 | Slave08 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16700 | Slave08 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16701 | Slave08 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16702 | Slave08 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16703 | Slave08 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16704 | Slave08 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16705 | Slave08 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16706 | Slave08 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16707 | Slave08 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16708 | Slave08 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16709 | Slave08 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16710 | Slave08 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16711 | Slave08 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16712 | Slave08 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16713 | Slave08 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16714 | Slave08 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16715 | Slave08 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16716 | Slave08 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16717 | Slave08 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16718 | Slave08 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16719 | Slave08 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16720 | Slave09 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16721 | Slave09 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16722 | Slave09 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16723 | Slave09 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16724 | Slave09 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16725 | Slave09 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16726 | Slave09 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16727 | Slave09 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16728 | Slave09 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16729 | Slave09 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16730 | Slave09 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16731 | Slave09 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16732 | Slave09 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16733 | Slave09 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16734 | Slave09 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16735 | Slave09 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16736 | Slave09 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16737 | Slave09 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16738 | Slave09 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16739 | Slave09 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16740 | Slave09 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16741 | Slave09 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16742 | Slave09 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16743 | Slave09 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16744 | Slave09 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16745 | Slave09 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16746 | Slave09 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16747 | Slave09 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16748 | Slave09 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16749 | Slave09 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16750 | Slave09 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16751 | Slave09 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16752 | Slave09 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16753 | Slave09 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16754 | Slave09 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16755 | Slave09 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16756 | Slave09 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16757 | Slave09 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16758 | Slave09 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16759 | Slave09 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16760 | Slave09 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16761 | Slave09 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16762 | Slave09 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16763 | Slave09 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16764 | Slave09 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16765 | Slave09 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16766 | Slave09 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16767 | Slave09 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16768 | Slave10 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16769 | Slave10 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16770 | Slave10 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16771 | Slave10 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16772 | Slave10 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16773 | Slave10 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16774 | Slave10 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16775 | Slave10 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16776 | Slave10 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16777 | Slave10 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16778 | Slave10 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16779 | Slave10 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16780 | Slave10 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16781 | Slave10 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16782 | Slave10 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16783 | Slave10 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16784 | Slave10 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16785 | Slave10 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16786 | Slave10 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16787 | Slave10 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16788 | Slave10 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16789 | Slave10 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16790 | Slave10 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16791 | Slave10 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16792 | Slave10 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16793 | Slave10 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16794 | Slave10 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16795 | Slave10 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16796 | Slave10 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16797 | Slave10 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16798 | Slave10 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16799 | Slave10 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16800 | Slave10 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16801 | Slave10 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16802 | Slave10 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16803 | Slave10 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16804 | Slave10 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16805 | Slave10 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16806 | Slave10 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16807 | Slave10 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16808 | Slave10 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16809 | Slave10 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16810 | Slave10 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16811 | Slave10 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16812 | Slave10 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16813 | Slave10 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16814 | Slave10 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16815 | Slave10 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16816 | Slave11 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16817 | Slave11 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16818 | Slave11 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16819 | Slave11 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16820 | Slave11 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16821 | Slave11 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16822 | Slave11 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16823 | Slave11 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16824 | Slave11 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16825 | Slave11 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16826 | Slave11 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16827 | Slave11 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16828 | Slave11 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16829 | Slave11 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16830 | Slave11 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16831 | Slave11 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16832 | Slave11 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16833 | Slave11 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16834 | Slave11 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16835 | Slave11 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16836 | Slave11 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16837 | Slave11 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16838 | Slave11 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16839 | Slave11 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16840 | Slave11 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16841 | Slave11 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16842 | Slave11 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16843 | Slave11 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16844 | Slave11 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16845 | Slave11 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16846 | Slave11 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16847 | Slave11 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16848 | Slave11 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16849 | Slave11 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16850 | Slave11 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16851 | Slave11 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16852 | Slave11 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16853 | Slave11 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16854 | Slave11 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16855 | Slave11 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16856 | Slave11 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16857 | Slave11 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16858 | Slave11 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16859 | Slave11 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16860 | Slave11 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16861 | Slave11 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16862 | Slave11 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16863 | Slave11 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16864 | Slave12 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16865 | Slave12 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16866 | Slave12 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16867 | Slave12 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16868 | Slave12 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16869 | Slave12 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16870 | Slave12 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16871 | Slave12 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16872 | Slave12 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16873 | Slave12 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16874 | Slave12 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16875 | Slave12 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16876 | Slave12 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16877 | Slave12 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16878 | Slave12 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16879 | Slave12 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16880 | Slave12 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16881 | Slave12 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16882 | Slave12 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16883 | Slave12 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16884 | Slave12 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16885 | Slave12 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16886 | Slave12 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16887 | Slave12 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16888 | Slave12 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16889 | Slave12 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16890 | Slave12 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16891 | Slave12 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16892 | Slave12 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16893 | Slave12 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16894 | Slave12 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16895 | Slave12 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16896 | Slave12 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16897 | Slave12 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16898 | Slave12 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16899 | Slave12 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16900 | Slave12 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16901 | Slave12 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16902 | Slave12 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16903 | Slave12 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16904 | Slave12 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16905 | Slave12 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16906 | Slave12 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16907 | Slave12 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16908 | Slave12 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16909 | Slave12 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16910 | Slave12 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16911 | Slave12 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16912 | Slave13 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16913 | Slave13 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16914 | Slave13 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16915 | Slave13 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16916 | Slave13 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16917 | Slave13 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16918 | Slave13 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16919 | Slave13 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16920 | Slave13 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16921 | Slave13 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16922 | Slave13 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16923 | Slave13 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16924 | Slave13 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16925 | Slave13 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16926 | Slave13 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16927 | Slave13 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16928 | Slave13 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16929 | Slave13 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16930 | Slave13 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16931 | Slave13 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16932 | Slave13 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16933 | Slave13 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16934 | Slave13 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16935 | Slave13 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16936 | Slave13 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16937 | Slave13 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16938 | Slave13 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16939 | Slave13 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16940 | Slave13 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16941 | Slave13 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16942 | Slave13 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16943 | Slave13 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16944 | Slave13 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16945 | Slave13 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16946 | Slave13 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16947 | Slave13 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16948 | Slave13 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16949 | Slave13 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16950 | Slave13 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16951 | Slave13 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
16952 | Slave13 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
16953 | Slave13 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
16954 | Slave13 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
16955 | Slave13 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
16956 | Slave13 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
16957 | Slave13 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
16958 | Slave13 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
16959 | Slave13 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
16960 | Slave14 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
16961 | Slave14 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
16962 | Slave14 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
16963 | Slave14 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
16964 | Slave14 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
16965 | Slave14 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
16966 | Slave14 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
16967 | Slave14 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
16968 | Slave14 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
16969 | Slave14 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
16970 | Slave14 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
16971 | Slave14 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
16972 | Slave14 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
16973 | Slave14 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
16974 | Slave14 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
16975 | Slave14 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
16976 | Slave14 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
16977 | Slave14 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
16978 | Slave14 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
16979 | Slave14 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
16980 | Slave14 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
16981 | Slave14 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
16982 | Slave14 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
16983 | Slave14 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
16984 | Slave14 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
16985 | Slave14 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
16986 | Slave14 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
16987 | Slave14 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
16988 | Slave14 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
16989 | Slave14 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
16990 | Slave14 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
16991 | Slave14 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
16992 | Slave14 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
16993 | Slave14 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
16994 | Slave14 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
16995 | Slave14 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
16996 | Slave14 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
16997 | Slave14 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
16998 | Slave14 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
16999 | Slave14 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
17000 | Slave14 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
17001 | Slave14 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
17002 | Slave14 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
17003 | Slave14 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
17004 | Slave14 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
17005 | Slave14 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
17006 | Slave14 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
17007 | Slave14 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
17008 | Slave15 Outlet Port01 Over Current Critical | RW | 2 bytes | Unit:0.01A
17009 | Slave15 Outlet Port02 Over Current Critical | RW | 2 bytes | Unit:0.01A
17010 | Slave15 Outlet Port03 Over Current Critical | RW | 2 bytes | Unit:0.01A
17011 | Slave15 Outlet Port04 Over Current Critical | RW | 2 bytes | Unit:0.01A
17012 | Slave15 Outlet Port05 Over Current Critical | RW | 2 bytes | Unit:0.01A
17013 | Slave15 Outlet Port06 Over Current Critical | RW | 2 bytes | Unit:0.01A
17014 | Slave15 Outlet Port07 Over Current Critical | RW | 2 bytes | Unit:0.01A
17015 | Slave15 Outlet Port08 Over Current Critical | RW | 2 bytes | Unit:0.01A
17016 | Slave15 Outlet Port09 Over Current Critical | RW | 2 bytes | Unit:0.01A
17017 | Slave15 Outlet Port10 Over Current Critical | RW | 2 bytes | Unit:0.01A
17018 | Slave15 Outlet Port11 Over Current Critical | RW | 2 bytes | Unit:0.01A
17019 | Slave15 Outlet Port12 Over Current Critical | RW | 2 bytes | Unit:0.01A
17020 | Slave15 Outlet Port13 Over Current Critical | RW | 2 bytes | Unit:0.01A
17021 | Slave15 Outlet Port14 Over Current Critical | RW | 2 bytes | Unit:0.01A
17022 | Slave15 Outlet Port15 Over Current Critical | RW | 2 bytes | Unit:0.01A
17023 | Slave15 Outlet Port16 Over Current Critical | RW | 2 bytes | Unit:0.01A
17024 | Slave15 Outlet Port17 Over Current Critical | RW | 2 bytes | Unit:0.01A
17025 | Slave15 Outlet Port18 Over Current Critical | RW | 2 bytes | Unit:0.01A
17026 | Slave15 Outlet Port19 Over Current Critical | RW | 2 bytes | Unit:0.01A
17027 | Slave15 Outlet Port20 Over Current Critical | RW | 2 bytes | Unit:0.01A
17028 | Slave15 Outlet Port21 Over Current Critical | RW | 2 bytes | Unit:0.01A
17029 | Slave15 Outlet Port22 Over Current Critical | RW | 2 bytes | Unit:0.01A
17030 | Slave15 Outlet Port23 Over Current Critical | RW | 2 bytes | Unit:0.01A
17031 | Slave15 Outlet Port24 Over Current Critical | RW | 2 bytes | Unit:0.01A
17032 | Slave15 Outlet Port25 Over Current Critical | RW | 2 bytes | Unit:0.01A
17033 | Slave15 Outlet Port26 Over Current Critical | RW | 2 bytes | Unit:0.01A
17034 | Slave15 Outlet Port27 Over Current Critical | RW | 2 bytes | Unit:0.01A
17035 | Slave15 Outlet Port28 Over Current Critical | RW | 2 bytes | Unit:0.01A
17036 | Slave15 Outlet Port29 Over Current Critical | RW | 2 bytes | Unit:0.01A
17037 | Slave15 Outlet Port30 Over Current Critical | RW | 2 bytes | Unit:0.01A
17038 | Slave15 Outlet Port31 Over Current Critical | RW | 2 bytes | Unit:0.01A
17039 | Slave15 Outlet Port32 Over Current Critical | RW | 2 bytes | Unit:0.01A
17040 | Slave15 Outlet Port33 Over Current Critical | RW | 2 bytes | Unit:0.01A
17041 | Slave15 Outlet Port34 Over Current Critical | RW | 2 bytes | Unit:0.01A
17042 | Slave15 Outlet Port35 Over Current Critical | RW | 2 bytes | Unit:0.01A
17043 | Slave15 Outlet Port36 Over Current Critical | RW | 2 bytes | Unit:0.01A
17044 | Slave15 Outlet Port37 Over Current Critical | RW | 2 bytes | Unit:0.01A
17045 | Slave15 Outlet Port38 Over Current Critical | RW | 2 bytes | Unit:0.01A
17046 | Slave15 Outlet Port39 Over Current Critical | RW | 2 bytes | Unit:0.01A
17047 | Slave15 Outlet Port40 Over Current Critical | RW | 2 bytes | Unit:0.01A
17048 | Slave15 Outlet Port41 Over Current Critical | RW | 2 bytes | Unit:0.01A
17049 | Slave15 Outlet Port42 Over Current Critical | RW | 2 bytes | Unit:0.01A
17050 | Slave15 Outlet Port43 Over Current Critical | RW | 2 bytes | Unit:0.01A
17051 | Slave15 Outlet Port44 Over Current Critical | RW | 2 bytes | Unit:0.01A
17052 | Slave15 Outlet Port45 Over Current Critical | RW | 2 bytes | Unit:0.01A
17053 | Slave15 Outlet Port46 Over Current Critical | RW | 2 bytes | Unit:0.01A
17054 | Slave15 Outlet Port47 Over Current Critical | RW | 2 bytes | Unit:0.01A
17055 | Slave15 Outlet Port48 Over Current Critical | RW | 2 bytes | Unit:0.01A
17056 | Master Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17057 | Master Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17058 | Master Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17059 | Master Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17060 | Master Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17061 | Master Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17062 | Master Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17063 | Master Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17064 | Master Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17065 | Master Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17066 | Master Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17067 | Master Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17068 | Master Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17069 | Master Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17070 | Master Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17071 | Master Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17072 | Master Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17073 | Master Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17074 | Master Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17075 | Master Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17076 | Master Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17077 | Master Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17078 | Master Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17079 | Master Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17080 | Master Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17081 | Master Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17082 | Master Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17083 | Master Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17084 | Master Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17085 | Master Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17086 | Master Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17087 | Master Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17088 | Master Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17089 | Master Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17090 | Master Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17091 | Master Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17092 | Master Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17093 | Master Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17094 | Master Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17095 | Master Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17096 | Master Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17097 | Master Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17098 | Master Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17099 | Master Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17100 | Master Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17101 | Master Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17102 | Master Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17103 | Master Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17104 | Slave01 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17105 | Slave01 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17106 | Slave01 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17107 | Slave01 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17108 | Slave01 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17109 | Slave01 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17110 | Slave01 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17111 | Slave01 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17112 | Slave01 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17113 | Slave01 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17114 | Slave01 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17115 | Slave01 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17116 | Slave01 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17117 | Slave01 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17118 | Slave01 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17119 | Slave01 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17120 | Slave01 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17121 | Slave01 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17122 | Slave01 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17123 | Slave01 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17124 | Slave01 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17125 | Slave01 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17126 | Slave01 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17127 | Slave01 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17128 | Slave01 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17129 | Slave01 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17130 | Slave01 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17131 | Slave01 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17132 | Slave01 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17133 | Slave01 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17134 | Slave01 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17135 | Slave01 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17136 | Slave01 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17137 | Slave01 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17138 | Slave01 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17139 | Slave01 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17140 | Slave01 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17141 | Slave01 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17142 | Slave01 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17143 | Slave01 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17144 | Slave01 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17145 | Slave01 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17146 | Slave01 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17147 | Slave01 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17148 | Slave01 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17149 | Slave01 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17150 | Slave01 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17151 | Slave01 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17152 | Slave02 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17153 | Slave02 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17154 | Slave02 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17155 | Slave02 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17156 | Slave02 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17157 | Slave02 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17158 | Slave02 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17159 | Slave02 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17160 | Slave02 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17161 | Slave02 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17162 | Slave02 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17163 | Slave02 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17164 | Slave02 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17165 | Slave02 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17166 | Slave02 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17167 | Slave02 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17168 | Slave02 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17169 | Slave02 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17170 | Slave02 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17171 | Slave02 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17172 | Slave02 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17173 | Slave02 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17174 | Slave02 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17175 | Slave02 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17176 | Slave02 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17177 | Slave02 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17178 | Slave02 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17179 | Slave02 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17180 | Slave02 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17181 | Slave02 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17182 | Slave02 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17183 | Slave02 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17184 | Slave02 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17185 | Slave02 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17186 | Slave02 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17187 | Slave02 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17188 | Slave02 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17189 | Slave02 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17190 | Slave02 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17191 | Slave02 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17192 | Slave02 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17193 | Slave02 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17194 | Slave02 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17195 | Slave02 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17196 | Slave02 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17197 | Slave02 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17198 | Slave02 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17199 | Slave02 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17200 | Slave03 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17201 | Slave03 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17202 | Slave03 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17203 | Slave03 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17204 | Slave03 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17205 | Slave03 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17206 | Slave03 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17207 | Slave03 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17208 | Slave03 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17209 | Slave03 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17210 | Slave03 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17211 | Slave03 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17212 | Slave03 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17213 | Slave03 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17214 | Slave03 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17215 | Slave03 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17216 | Slave03 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17217 | Slave03 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17218 | Slave03 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17219 | Slave03 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17220 | Slave03 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17221 | Slave03 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17222 | Slave03 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17223 | Slave03 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17224 | Slave03 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17225 | Slave03 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17226 | Slave03 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17227 | Slave03 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17228 | Slave03 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17229 | Slave03 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17230 | Slave03 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17231 | Slave03 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17232 | Slave03 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17233 | Slave03 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17234 | Slave03 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17235 | Slave03 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17236 | Slave03 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17237 | Slave03 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17238 | Slave03 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17239 | Slave03 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17240 | Slave03 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17241 | Slave03 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17242 | Slave03 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17243 | Slave03 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17244 | Slave03 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17245 | Slave03 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17246 | Slave03 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17247 | Slave03 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17248 | Slave04 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17249 | Slave04 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17250 | Slave04 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17251 | Slave04 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17252 | Slave04 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17253 | Slave04 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17254 | Slave04 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17255 | Slave04 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17256 | Slave04 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17257 | Slave04 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17258 | Slave04 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17259 | Slave04 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17260 | Slave04 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17261 | Slave04 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17262 | Slave04 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17263 | Slave04 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17264 | Slave04 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17265 | Slave04 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17266 | Slave04 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17267 | Slave04 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17268 | Slave04 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17269 | Slave04 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17270 | Slave04 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17271 | Slave04 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17272 | Slave04 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17273 | Slave04 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17274 | Slave04 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17275 | Slave04 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17276 | Slave04 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17277 | Slave04 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17278 | Slave04 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17279 | Slave04 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17280 | Slave04 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17281 | Slave04 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17282 | Slave04 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17283 | Slave04 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17284 | Slave04 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17285 | Slave04 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17286 | Slave04 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17287 | Slave04 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17288 | Slave04 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17289 | Slave04 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17290 | Slave04 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17291 | Slave04 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17292 | Slave04 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17293 | Slave04 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17294 | Slave04 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17295 | Slave04 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17296 | Slave05 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17297 | Slave05 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17298 | Slave05 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17299 | Slave05 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17300 | Slave05 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17301 | Slave05 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17302 | Slave05 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17303 | Slave05 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17304 | Slave05 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17305 | Slave05 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17306 | Slave05 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17307 | Slave05 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17308 | Slave05 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17309 | Slave05 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17310 | Slave05 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17311 | Slave05 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17312 | Slave05 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17313 | Slave05 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17314 | Slave05 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17315 | Slave05 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17316 | Slave05 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17317 | Slave05 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17318 | Slave05 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17319 | Slave05 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17320 | Slave05 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17321 | Slave05 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17322 | Slave05 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17323 | Slave05 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17324 | Slave05 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17325 | Slave05 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17326 | Slave05 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17327 | Slave05 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17328 | Slave05 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17329 | Slave05 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17330 | Slave05 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17331 | Slave05 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17332 | Slave05 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17333 | Slave05 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17334 | Slave05 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17335 | Slave05 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17336 | Slave05 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17337 | Slave05 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17338 | Slave05 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17339 | Slave05 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17340 | Slave05 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17341 | Slave05 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17342 | Slave05 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17343 | Slave05 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17344 | Slave06 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17345 | Slave06 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17346 | Slave06 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17347 | Slave06 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17348 | Slave06 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17349 | Slave06 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17350 | Slave06 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17351 | Slave06 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17352 | Slave06 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17353 | Slave06 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17354 | Slave06 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17355 | Slave06 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17356 | Slave06 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17357 | Slave06 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17358 | Slave06 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17359 | Slave06 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17360 | Slave06 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17361 | Slave06 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17362 | Slave06 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17363 | Slave06 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17364 | Slave06 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17365 | Slave06 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17366 | Slave06 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17367 | Slave06 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17368 | Slave06 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17369 | Slave06 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17370 | Slave06 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17371 | Slave06 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17372 | Slave06 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17373 | Slave06 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17374 | Slave06 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17375 | Slave06 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17376 | Slave06 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17377 | Slave06 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17378 | Slave06 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17379 | Slave06 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17380 | Slave06 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17381 | Slave06 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17382 | Slave06 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17383 | Slave06 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17384 | Slave06 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17385 | Slave06 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17386 | Slave06 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17387 | Slave06 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17388 | Slave06 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17389 | Slave06 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17390 | Slave06 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17391 | Slave06 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17392 | Slave07 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17393 | Slave07 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17394 | Slave07 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17395 | Slave07 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17396 | Slave07 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17397 | Slave07 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17398 | Slave07 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17399 | Slave07 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17400 | Slave07 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17401 | Slave07 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17402 | Slave07 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17403 | Slave07 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17404 | Slave07 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17405 | Slave07 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17406 | Slave07 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17407 | Slave07 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17408 | Slave07 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17409 | Slave07 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17410 | Slave07 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17411 | Slave07 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17412 | Slave07 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17413 | Slave07 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17414 | Slave07 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17415 | Slave07 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17416 | Slave07 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17417 | Slave07 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17418 | Slave07 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17419 | Slave07 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17420 | Slave07 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17421 | Slave07 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17422 | Slave07 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17423 | Slave07 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17424 | Slave07 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17425 | Slave07 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17426 | Slave07 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17427 | Slave07 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17428 | Slave07 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17429 | Slave07 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17430 | Slave07 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17431 | Slave07 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17432 | Slave07 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17433 | Slave07 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17434 | Slave07 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17435 | Slave07 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17436 | Slave07 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17437 | Slave07 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17438 | Slave07 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17439 | Slave07 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17440 | Slave08 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17441 | Slave08 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17442 | Slave08 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17443 | Slave08 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17444 | Slave08 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17445 | Slave08 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17446 | Slave08 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17447 | Slave08 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17448 | Slave08 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17449 | Slave08 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17450 | Slave08 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17451 | Slave08 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17452 | Slave08 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17453 | Slave08 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17454 | Slave08 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17455 | Slave08 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17456 | Slave08 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17457 | Slave08 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17458 | Slave08 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17459 | Slave08 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17460 | Slave08 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17461 | Slave08 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17462 | Slave08 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17463 | Slave08 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17464 | Slave08 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17465 | Slave08 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17466 | Slave08 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17467 | Slave08 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17468 | Slave08 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17469 | Slave08 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17470 | Slave08 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17471 | Slave08 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17472 | Slave08 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17473 | Slave08 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17474 | Slave08 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17475 | Slave08 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17476 | Slave08 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17477 | Slave08 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17478 | Slave08 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17479 | Slave08 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17480 | Slave08 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17481 | Slave08 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17482 | Slave08 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17483 | Slave08 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17484 | Slave08 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17485 | Slave08 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17486 | Slave08 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17487 | Slave08 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17488 | Slave09 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17489 | Slave09 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17490 | Slave09 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17491 | Slave09 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17492 | Slave09 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17493 | Slave09 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17494 | Slave09 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17495 | Slave09 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17496 | Slave09 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17497 | Slave09 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17498 | Slave09 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17499 | Slave09 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17500 | Slave09 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17501 | Slave09 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17502 | Slave09 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17503 | Slave09 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17504 | Slave09 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17505 | Slave09 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17506 | Slave09 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17507 | Slave09 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17508 | Slave09 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17509 | Slave09 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17510 | Slave09 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17511 | Slave09 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17512 | Slave09 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17513 | Slave09 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17514 | Slave09 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17515 | Slave09 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17516 | Slave09 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17517 | Slave09 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17518 | Slave09 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17519 | Slave09 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17520 | Slave09 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17521 | Slave09 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17522 | Slave09 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17523 | Slave09 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17524 | Slave09 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17525 | Slave09 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17526 | Slave09 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17527 | Slave09 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17528 | Slave09 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17529 | Slave09 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17530 | Slave09 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17531 | Slave09 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17532 | Slave09 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17533 | Slave09 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17534 | Slave09 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17535 | Slave09 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17536 | Slave10 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17537 | Slave10 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17538 | Slave10 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17539 | Slave10 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17540 | Slave10 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17541 | Slave10 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17542 | Slave10 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17543 | Slave10 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17544 | Slave10 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17545 | Slave10 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17546 | Slave10 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17547 | Slave10 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17548 | Slave10 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17549 | Slave10 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17550 | Slave10 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17551 | Slave10 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17552 | Slave10 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17553 | Slave10 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17554 | Slave10 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17555 | Slave10 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17556 | Slave10 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17557 | Slave10 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17558 | Slave10 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17559 | Slave10 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17560 | Slave10 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17561 | Slave10 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17562 | Slave10 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17563 | Slave10 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17564 | Slave10 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17565 | Slave10 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17566 | Slave10 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17567 | Slave10 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17568 | Slave10 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17569 | Slave10 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17570 | Slave10 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17571 | Slave10 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17572 | Slave10 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17573 | Slave10 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17574 | Slave10 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17575 | Slave10 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17576 | Slave10 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17577 | Slave10 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17578 | Slave10 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17579 | Slave10 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17580 | Slave10 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17581 | Slave10 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17582 | Slave10 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17583 | Slave10 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17584 | Slave11 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17585 | Slave11 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17586 | Slave11 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17587 | Slave11 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17588 | Slave11 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17589 | Slave11 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17590 | Slave11 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17591 | Slave11 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17592 | Slave11 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17593 | Slave11 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17594 | Slave11 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17595 | Slave11 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17596 | Slave11 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17597 | Slave11 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17598 | Slave11 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17599 | Slave11 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17600 | Slave11 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17601 | Slave11 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17602 | Slave11 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17603 | Slave11 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17604 | Slave11 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17605 | Slave11 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17606 | Slave11 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17607 | Slave11 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17608 | Slave11 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17609 | Slave11 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17610 | Slave11 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17611 | Slave11 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17612 | Slave11 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17613 | Slave11 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17614 | Slave11 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17615 | Slave11 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17616 | Slave11 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17617 | Slave11 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17618 | Slave11 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17619 | Slave11 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17620 | Slave11 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17621 | Slave11 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17622 | Slave11 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17623 | Slave11 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17624 | Slave11 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17625 | Slave11 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17626 | Slave11 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17627 | Slave11 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17628 | Slave11 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17629 | Slave11 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17630 | Slave11 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17631 | Slave11 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17632 | Slave12 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17633 | Slave12 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17634 | Slave12 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17635 | Slave12 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17636 | Slave12 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17637 | Slave12 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17638 | Slave12 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17639 | Slave12 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17640 | Slave12 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17641 | Slave12 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17642 | Slave12 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17643 | Slave12 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17644 | Slave12 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17645 | Slave12 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17646 | Slave12 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17647 | Slave12 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17648 | Slave12 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17649 | Slave12 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17650 | Slave12 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17651 | Slave12 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17652 | Slave12 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17653 | Slave12 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17654 | Slave12 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17655 | Slave12 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17656 | Slave12 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17657 | Slave12 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17658 | Slave12 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17659 | Slave12 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17660 | Slave12 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17661 | Slave12 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17662 | Slave12 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17663 | Slave12 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17664 | Slave12 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17665 | Slave12 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17666 | Slave12 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17667 | Slave12 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17668 | Slave12 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17669 | Slave12 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17670 | Slave12 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17671 | Slave12 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17672 | Slave12 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17673 | Slave12 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17674 | Slave12 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17675 | Slave12 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17676 | Slave12 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17677 | Slave12 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17678 | Slave12 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17679 | Slave12 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17680 | Slave13 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17681 | Slave13 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17682 | Slave13 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17683 | Slave13 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17684 | Slave13 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17685 | Slave13 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17686 | Slave13 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17687 | Slave13 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17688 | Slave13 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17689 | Slave13 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17690 | Slave13 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17691 | Slave13 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17692 | Slave13 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17693 | Slave13 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17694 | Slave13 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17695 | Slave13 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17696 | Slave13 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17697 | Slave13 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17698 | Slave13 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17699 | Slave13 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17700 | Slave13 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17701 | Slave13 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17702 | Slave13 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17703 | Slave13 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17704 | Slave13 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17705 | Slave13 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17706 | Slave13 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17707 | Slave13 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17708 | Slave13 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17709 | Slave13 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17710 | Slave13 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17711 | Slave13 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17712 | Slave13 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17713 | Slave13 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17714 | Slave13 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17715 | Slave13 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17716 | Slave13 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17717 | Slave13 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17718 | Slave13 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17719 | Slave13 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17720 | Slave13 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17721 | Slave13 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17722 | Slave13 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17723 | Slave13 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17724 | Slave13 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17725 | Slave13 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17726 | Slave13 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17727 | Slave13 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17728 | Slave14 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17729 | Slave14 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17730 | Slave14 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17731 | Slave14 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17732 | Slave14 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17733 | Slave14 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17734 | Slave14 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17735 | Slave14 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17736 | Slave14 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17737 | Slave14 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17738 | Slave14 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17739 | Slave14 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17740 | Slave14 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17741 | Slave14 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17742 | Slave14 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17743 | Slave14 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17744 | Slave14 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17745 | Slave14 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17746 | Slave14 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17747 | Slave14 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17748 | Slave14 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17749 | Slave14 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17750 | Slave14 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17751 | Slave14 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17752 | Slave14 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17753 | Slave14 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17754 | Slave14 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17755 | Slave14 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17756 | Slave14 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17757 | Slave14 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17758 | Slave14 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17759 | Slave14 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17760 | Slave14 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17761 | Slave14 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17762 | Slave14 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17763 | Slave14 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17764 | Slave14 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17765 | Slave14 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17766 | Slave14 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17767 | Slave14 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17768 | Slave14 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17769 | Slave14 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17770 | Slave14 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17771 | Slave14 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17772 | Slave14 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17773 | Slave14 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17774 | Slave14 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17775 | Slave14 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17776 | Slave15 Outlet Port01 Over Power Warning | RW | 2 bytes | Unit:1
17777 | Slave15 Outlet Port02 Over Power Warning | RW | 2 bytes | Unit:1
17778 | Slave15 Outlet Port03 Over Power Warning | RW | 2 bytes | Unit:1
17779 | Slave15 Outlet Port04 Over Power Warning | RW | 2 bytes | Unit:1
17780 | Slave15 Outlet Port05 Over Power Warning | RW | 2 bytes | Unit:1
17781 | Slave15 Outlet Port06 Over Power Warning | RW | 2 bytes | Unit:1
17782 | Slave15 Outlet Port07 Over Power Warning | RW | 2 bytes | Unit:1
17783 | Slave15 Outlet Port08 Over Power Warning | RW | 2 bytes | Unit:1
17784 | Slave15 Outlet Port09 Over Power Warning | RW | 2 bytes | Unit:1
17785 | Slave15 Outlet Port10 Over Power Warning | RW | 2 bytes | Unit:1
17786 | Slave15 Outlet Port11 Over Power Warning | RW | 2 bytes | Unit:1
17787 | Slave15 Outlet Port12 Over Power Warning | RW | 2 bytes | Unit:1
17788 | Slave15 Outlet Port13 Over Power Warning | RW | 2 bytes | Unit:1
17789 | Slave15 Outlet Port14 Over Power Warning | RW | 2 bytes | Unit:1
17790 | Slave15 Outlet Port15 Over Power Warning | RW | 2 bytes | Unit:1
17791 | Slave15 Outlet Port16 Over Power Warning | RW | 2 bytes | Unit:1
17792 | Slave15 Outlet Port17 Over Power Warning | RW | 2 bytes | Unit:1
17793 | Slave15 Outlet Port18 Over Power Warning | RW | 2 bytes | Unit:1
17794 | Slave15 Outlet Port19 Over Power Warning | RW | 2 bytes | Unit:1
17795 | Slave15 Outlet Port20 Over Power Warning | RW | 2 bytes | Unit:1
17796 | Slave15 Outlet Port21 Over Power Warning | RW | 2 bytes | Unit:1
17797 | Slave15 Outlet Port22 Over Power Warning | RW | 2 bytes | Unit:1
17798 | Slave15 Outlet Port23 Over Power Warning | RW | 2 bytes | Unit:1
17799 | Slave15 Outlet Port24 Over Power Warning | RW | 2 bytes | Unit:1
17800 | Slave15 Outlet Port25 Over Power Warning | RW | 2 bytes | Unit:1
17801 | Slave15 Outlet Port26 Over Power Warning | RW | 2 bytes | Unit:1
17802 | Slave15 Outlet Port27 Over Power Warning | RW | 2 bytes | Unit:1
17803 | Slave15 Outlet Port28 Over Power Warning | RW | 2 bytes | Unit:1
17804 | Slave15 Outlet Port29 Over Power Warning | RW | 2 bytes | Unit:1
17805 | Slave15 Outlet Port30 Over Power Warning | RW | 2 bytes | Unit:1
17806 | Slave15 Outlet Port31 Over Power Warning | RW | 2 bytes | Unit:1
17807 | Slave15 Outlet Port32 Over Power Warning | RW | 2 bytes | Unit:1
17808 | Slave15 Outlet Port33 Over Power Warning | RW | 2 bytes | Unit:1
17809 | Slave15 Outlet Port34 Over Power Warning | RW | 2 bytes | Unit:1
17810 | Slave15 Outlet Port35 Over Power Warning | RW | 2 bytes | Unit:1
17811 | Slave15 Outlet Port36 Over Power Warning | RW | 2 bytes | Unit:1
17812 | Slave15 Outlet Port37 Over Power Warning | RW | 2 bytes | Unit:1
17813 | Slave15 Outlet Port38 Over Power Warning | RW | 2 bytes | Unit:1
17814 | Slave15 Outlet Port39 Over Power Warning | RW | 2 bytes | Unit:1
17815 | Slave15 Outlet Port40 Over Power Warning | RW | 2 bytes | Unit:1
17816 | Slave15 Outlet Port41 Over Power Warning | RW | 2 bytes | Unit:1
17817 | Slave15 Outlet Port42 Over Power Warning | RW | 2 bytes | Unit:1
17818 | Slave15 Outlet Port43 Over Power Warning | RW | 2 bytes | Unit:1
17819 | Slave15 Outlet Port44 Over Power Warning | RW | 2 bytes | Unit:1
17820 | Slave15 Outlet Port45 Over Power Warning | RW | 2 bytes | Unit:1
17821 | Slave15 Outlet Port46 Over Power Warning | RW | 2 bytes | Unit:1
17822 | Slave15 Outlet Port47 Over Power Warning | RW | 2 bytes | Unit:1
17823 | Slave15 Outlet Port48 Over Power Warning | RW | 2 bytes | Unit:1
17824 | Master Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
17825 | Master Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
17826 | Master Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
17827 | Master Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
17828 | Master Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
17829 | Master Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
17830 | Master Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
17831 | Master Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
17832 | Master Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
17833 | Master Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
17834 | Master Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
17835 | Master Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
17836 | Master Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
17837 | Master Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
17838 | Master Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
17839 | Master Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
17840 | Master Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
17841 | Master Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
17842 | Master Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
17843 | Master Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
17844 | Master Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
17845 | Master Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
17846 | Master Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
17847 | Master Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
17848 | Master Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
17849 | Master Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
17850 | Master Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
17851 | Master Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
17852 | Master Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
17853 | Master Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
17854 | Master Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
17855 | Master Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
17856 | Master Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
17857 | Master Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
17858 | Master Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
17859 | Master Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
17860 | Master Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
17861 | Master Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
17862 | Master Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
17863 | Master Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
17864 | Master Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
17865 | Master Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
17866 | Master Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
17867 | Master Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
17868 | Master Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
17869 | Master Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
17870 | Master Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
17871 | Master Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
17872 | Slave01 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
17873 | Slave01 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
17874 | Slave01 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
17875 | Slave01 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
17876 | Slave01 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
17877 | Slave01 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
17878 | Slave01 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
17879 | Slave01 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
17880 | Slave01 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
17881 | Slave01 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
17882 | Slave01 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
17883 | Slave01 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
17884 | Slave01 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
17885 | Slave01 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
17886 | Slave01 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
17887 | Slave01 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
17888 | Slave01 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
17889 | Slave01 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
17890 | Slave01 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
17891 | Slave01 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
17892 | Slave01 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
17893 | Slave01 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
17894 | Slave01 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
17895 | Slave01 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
17896 | Slave01 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
17897 | Slave01 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
17898 | Slave01 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
17899 | Slave01 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
17900 | Slave01 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
17901 | Slave01 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
17902 | Slave01 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
17903 | Slave01 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
17904 | Slave01 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
17905 | Slave01 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
17906 | Slave01 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
17907 | Slave01 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
17908 | Slave01 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
17909 | Slave01 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
17910 | Slave01 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
17911 | Slave01 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
17912 | Slave01 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
17913 | Slave01 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
17914 | Slave01 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
17915 | Slave01 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
17916 | Slave01 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
17917 | Slave01 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
17918 | Slave01 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
17919 | Slave01 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
17920 | Slave02 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
17921 | Slave02 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
17922 | Slave02 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
17923 | Slave02 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
17924 | Slave02 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
17925 | Slave02 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
17926 | Slave02 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
17927 | Slave02 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
17928 | Slave02 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
17929 | Slave02 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
17930 | Slave02 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
17931 | Slave02 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
17932 | Slave02 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
17933 | Slave02 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
17934 | Slave02 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
17935 | Slave02 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
17936 | Slave02 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
17937 | Slave02 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
17938 | Slave02 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
17939 | Slave02 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
17940 | Slave02 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
17941 | Slave02 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
17942 | Slave02 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
17943 | Slave02 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
17944 | Slave02 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
17945 | Slave02 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
17946 | Slave02 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
17947 | Slave02 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
17948 | Slave02 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
17949 | Slave02 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
17950 | Slave02 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
17951 | Slave02 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
17952 | Slave02 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
17953 | Slave02 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
17954 | Slave02 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
17955 | Slave02 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
17956 | Slave02 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
17957 | Slave02 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
17958 | Slave02 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
17959 | Slave02 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
17960 | Slave02 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
17961 | Slave02 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
17962 | Slave02 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
17963 | Slave02 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
17964 | Slave02 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
17965 | Slave02 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
17966 | Slave02 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
17967 | Slave02 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
17968 | Slave03 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
17969 | Slave03 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
17970 | Slave03 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
17971 | Slave03 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
17972 | Slave03 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
17973 | Slave03 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
17974 | Slave03 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
17975 | Slave03 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
17976 | Slave03 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
17977 | Slave03 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
17978 | Slave03 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
17979 | Slave03 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
17980 | Slave03 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
17981 | Slave03 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
17982 | Slave03 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
17983 | Slave03 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
17984 | Slave03 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
17985 | Slave03 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
17986 | Slave03 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
17987 | Slave03 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
17988 | Slave03 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
17989 | Slave03 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
17990 | Slave03 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
17991 | Slave03 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
17992 | Slave03 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
17993 | Slave03 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
17994 | Slave03 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
17995 | Slave03 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
17996 | Slave03 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
17997 | Slave03 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
17998 | Slave03 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
17999 | Slave03 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18000 | Slave03 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18001 | Slave03 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18002 | Slave03 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18003 | Slave03 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18004 | Slave03 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18005 | Slave03 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18006 | Slave03 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18007 | Slave03 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18008 | Slave03 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18009 | Slave03 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18010 | Slave03 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18011 | Slave03 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18012 | Slave03 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18013 | Slave03 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18014 | Slave03 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18015 | Slave03 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18016 | Slave04 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18017 | Slave04 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18018 | Slave04 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18019 | Slave04 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18020 | Slave04 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18021 | Slave04 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18022 | Slave04 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18023 | Slave04 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18024 | Slave04 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18025 | Slave04 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18026 | Slave04 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18027 | Slave04 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18028 | Slave04 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18029 | Slave04 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18030 | Slave04 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18031 | Slave04 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18032 | Slave04 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18033 | Slave04 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18034 | Slave04 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18035 | Slave04 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18036 | Slave04 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18037 | Slave04 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18038 | Slave04 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18039 | Slave04 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18040 | Slave04 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18041 | Slave04 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18042 | Slave04 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18043 | Slave04 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18044 | Slave04 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18045 | Slave04 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18046 | Slave04 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18047 | Slave04 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18048 | Slave04 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18049 | Slave04 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18050 | Slave04 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18051 | Slave04 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18052 | Slave04 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18053 | Slave04 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18054 | Slave04 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18055 | Slave04 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18056 | Slave04 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18057 | Slave04 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18058 | Slave04 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18059 | Slave04 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18060 | Slave04 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18061 | Slave04 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18062 | Slave04 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18063 | Slave04 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18064 | Slave05 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18065 | Slave05 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18066 | Slave05 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18067 | Slave05 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18068 | Slave05 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18069 | Slave05 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18070 | Slave05 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18071 | Slave05 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18072 | Slave05 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18073 | Slave05 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18074 | Slave05 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18075 | Slave05 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18076 | Slave05 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18077 | Slave05 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18078 | Slave05 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18079 | Slave05 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18080 | Slave05 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18081 | Slave05 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18082 | Slave05 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18083 | Slave05 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18084 | Slave05 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18085 | Slave05 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18086 | Slave05 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18087 | Slave05 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18088 | Slave05 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18089 | Slave05 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18090 | Slave05 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18091 | Slave05 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18092 | Slave05 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18093 | Slave05 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18094 | Slave05 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18095 | Slave05 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18096 | Slave05 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18097 | Slave05 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18098 | Slave05 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18099 | Slave05 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18100 | Slave05 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18101 | Slave05 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18102 | Slave05 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18103 | Slave05 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18104 | Slave05 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18105 | Slave05 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18106 | Slave05 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18107 | Slave05 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18108 | Slave05 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18109 | Slave05 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18110 | Slave05 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18111 | Slave05 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18112 | Slave06 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18113 | Slave06 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18114 | Slave06 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18115 | Slave06 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18116 | Slave06 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18117 | Slave06 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18118 | Slave06 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18119 | Slave06 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18120 | Slave06 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18121 | Slave06 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18122 | Slave06 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18123 | Slave06 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18124 | Slave06 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18125 | Slave06 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18126 | Slave06 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18127 | Slave06 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18128 | Slave06 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18129 | Slave06 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18130 | Slave06 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18131 | Slave06 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18132 | Slave06 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18133 | Slave06 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18134 | Slave06 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18135 | Slave06 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18136 | Slave06 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18137 | Slave06 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18138 | Slave06 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18139 | Slave06 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18140 | Slave06 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18141 | Slave06 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18142 | Slave06 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18143 | Slave06 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18144 | Slave06 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18145 | Slave06 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18146 | Slave06 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18147 | Slave06 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18148 | Slave06 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18149 | Slave06 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18150 | Slave06 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18151 | Slave06 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18152 | Slave06 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18153 | Slave06 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18154 | Slave06 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18155 | Slave06 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18156 | Slave06 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18157 | Slave06 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18158 | Slave06 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18159 | Slave06 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18160 | Slave07 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18161 | Slave07 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18162 | Slave07 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18163 | Slave07 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18164 | Slave07 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18165 | Slave07 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18166 | Slave07 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18167 | Slave07 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18168 | Slave07 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18169 | Slave07 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18170 | Slave07 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18171 | Slave07 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18172 | Slave07 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18173 | Slave07 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18174 | Slave07 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18175 | Slave07 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18176 | Slave07 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18177 | Slave07 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18178 | Slave07 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18179 | Slave07 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18180 | Slave07 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18181 | Slave07 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18182 | Slave07 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18183 | Slave07 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18184 | Slave07 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18185 | Slave07 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18186 | Slave07 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18187 | Slave07 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18188 | Slave07 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18189 | Slave07 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18190 | Slave07 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18191 | Slave07 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18192 | Slave07 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18193 | Slave07 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18194 | Slave07 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18195 | Slave07 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18196 | Slave07 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18197 | Slave07 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18198 | Slave07 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18199 | Slave07 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18200 | Slave07 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18201 | Slave07 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18202 | Slave07 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18203 | Slave07 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18204 | Slave07 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18205 | Slave07 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18206 | Slave07 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18207 | Slave07 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18208 | Slave08 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18209 | Slave08 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18210 | Slave08 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18211 | Slave08 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18212 | Slave08 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18213 | Slave08 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18214 | Slave08 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18215 | Slave08 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18216 | Slave08 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18217 | Slave08 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18218 | Slave08 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18219 | Slave08 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18220 | Slave08 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18221 | Slave08 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18222 | Slave08 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18223 | Slave08 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18224 | Slave08 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18225 | Slave08 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18226 | Slave08 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18227 | Slave08 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18228 | Slave08 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18229 | Slave08 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18230 | Slave08 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18231 | Slave08 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18232 | Slave08 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18233 | Slave08 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18234 | Slave08 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18235 | Slave08 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18236 | Slave08 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18237 | Slave08 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18238 | Slave08 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18239 | Slave08 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18240 | Slave08 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18241 | Slave08 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18242 | Slave08 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18243 | Slave08 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18244 | Slave08 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18245 | Slave08 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18246 | Slave08 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18247 | Slave08 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18248 | Slave08 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18249 | Slave08 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18250 | Slave08 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18251 | Slave08 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18252 | Slave08 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18253 | Slave08 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18254 | Slave08 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18255 | Slave08 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18256 | Slave09 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18257 | Slave09 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18258 | Slave09 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18259 | Slave09 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18260 | Slave09 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18261 | Slave09 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18262 | Slave09 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18263 | Slave09 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18264 | Slave09 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18265 | Slave09 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18266 | Slave09 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18267 | Slave09 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18268 | Slave09 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18269 | Slave09 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18270 | Slave09 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18271 | Slave09 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18272 | Slave09 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18273 | Slave09 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18274 | Slave09 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18275 | Slave09 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18276 | Slave09 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18277 | Slave09 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18278 | Slave09 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18279 | Slave09 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18280 | Slave09 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18281 | Slave09 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18282 | Slave09 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18283 | Slave09 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18284 | Slave09 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18285 | Slave09 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18286 | Slave09 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18287 | Slave09 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18288 | Slave09 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18289 | Slave09 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18290 | Slave09 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18291 | Slave09 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18292 | Slave09 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18293 | Slave09 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18294 | Slave09 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18295 | Slave09 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18296 | Slave09 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18297 | Slave09 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18298 | Slave09 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18299 | Slave09 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18300 | Slave09 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18301 | Slave09 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18302 | Slave09 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18303 | Slave09 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18304 | Slave10 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18305 | Slave10 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18306 | Slave10 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18307 | Slave10 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18308 | Slave10 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18309 | Slave10 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18310 | Slave10 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18311 | Slave10 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18312 | Slave10 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18313 | Slave10 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18314 | Slave10 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18315 | Slave10 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18316 | Slave10 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18317 | Slave10 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18318 | Slave10 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18319 | Slave10 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18320 | Slave10 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18321 | Slave10 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18322 | Slave10 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18323 | Slave10 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18324 | Slave10 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18325 | Slave10 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18326 | Slave10 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18327 | Slave10 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18328 | Slave10 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18329 | Slave10 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18330 | Slave10 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18331 | Slave10 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18332 | Slave10 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18333 | Slave10 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18334 | Slave10 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18335 | Slave10 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18336 | Slave10 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18337 | Slave10 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18338 | Slave10 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18339 | Slave10 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18340 | Slave10 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18341 | Slave10 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18342 | Slave10 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18343 | Slave10 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18344 | Slave10 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18345 | Slave10 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18346 | Slave10 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18347 | Slave10 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18348 | Slave10 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18349 | Slave10 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18350 | Slave10 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18351 | Slave10 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18352 | Slave11 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18353 | Slave11 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18354 | Slave11 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18355 | Slave11 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18356 | Slave11 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18357 | Slave11 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18358 | Slave11 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18359 | Slave11 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18360 | Slave11 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18361 | Slave11 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18362 | Slave11 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18363 | Slave11 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18364 | Slave11 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18365 | Slave11 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18366 | Slave11 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18367 | Slave11 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18368 | Slave11 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18369 | Slave11 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18370 | Slave11 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18371 | Slave11 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18372 | Slave11 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18373 | Slave11 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18374 | Slave11 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18375 | Slave11 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18376 | Slave11 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18377 | Slave11 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18378 | Slave11 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18379 | Slave11 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18380 | Slave11 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18381 | Slave11 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18382 | Slave11 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18383 | Slave11 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18384 | Slave11 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18385 | Slave11 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18386 | Slave11 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18387 | Slave11 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18388 | Slave11 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18389 | Slave11 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18390 | Slave11 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18391 | Slave11 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18392 | Slave11 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18393 | Slave11 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18394 | Slave11 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18395 | Slave11 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18396 | Slave11 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18397 | Slave11 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18398 | Slave11 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18399 | Slave11 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18400 | Slave12 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18401 | Slave12 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18402 | Slave12 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18403 | Slave12 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18404 | Slave12 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18405 | Slave12 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18406 | Slave12 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18407 | Slave12 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18408 | Slave12 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18409 | Slave12 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18410 | Slave12 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18411 | Slave12 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18412 | Slave12 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18413 | Slave12 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18414 | Slave12 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18415 | Slave12 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18416 | Slave12 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18417 | Slave12 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18418 | Slave12 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18419 | Slave12 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18420 | Slave12 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18421 | Slave12 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18422 | Slave12 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18423 | Slave12 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18424 | Slave12 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18425 | Slave12 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18426 | Slave12 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18427 | Slave12 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18428 | Slave12 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18429 | Slave12 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18430 | Slave12 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18431 | Slave12 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18432 | Slave12 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18433 | Slave12 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18434 | Slave12 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18435 | Slave12 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18436 | Slave12 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18437 | Slave12 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18438 | Slave12 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18439 | Slave12 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18440 | Slave12 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18441 | Slave12 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18442 | Slave12 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18443 | Slave12 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18444 | Slave12 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18445 | Slave12 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18446 | Slave12 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18447 | Slave12 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18448 | Slave13 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18449 | Slave13 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18450 | Slave13 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18451 | Slave13 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18452 | Slave13 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18453 | Slave13 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18454 | Slave13 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18455 | Slave13 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18456 | Slave13 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18457 | Slave13 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18458 | Slave13 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18459 | Slave13 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18460 | Slave13 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18461 | Slave13 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18462 | Slave13 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18463 | Slave13 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18464 | Slave13 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18465 | Slave13 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18466 | Slave13 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18467 | Slave13 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18468 | Slave13 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18469 | Slave13 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18470 | Slave13 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18471 | Slave13 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18472 | Slave13 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18473 | Slave13 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18474 | Slave13 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18475 | Slave13 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18476 | Slave13 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18477 | Slave13 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18478 | Slave13 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18479 | Slave13 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18480 | Slave13 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18481 | Slave13 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18482 | Slave13 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18483 | Slave13 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18484 | Slave13 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18485 | Slave13 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18486 | Slave13 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18487 | Slave13 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18488 | Slave13 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18489 | Slave13 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18490 | Slave13 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18491 | Slave13 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18492 | Slave13 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18493 | Slave13 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18494 | Slave13 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18495 | Slave13 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18496 | Slave14 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18497 | Slave14 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18498 | Slave14 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18499 | Slave14 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18500 | Slave14 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18501 | Slave14 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18502 | Slave14 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18503 | Slave14 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18504 | Slave14 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18505 | Slave14 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18506 | Slave14 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18507 | Slave14 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18508 | Slave14 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18509 | Slave14 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18510 | Slave14 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18511 | Slave14 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18512 | Slave14 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18513 | Slave14 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18514 | Slave14 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18515 | Slave14 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18516 | Slave14 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18517 | Slave14 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18518 | Slave14 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18519 | Slave14 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18520 | Slave14 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18521 | Slave14 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18522 | Slave14 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18523 | Slave14 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18524 | Slave14 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18525 | Slave14 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18526 | Slave14 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18527 | Slave14 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18528 | Slave14 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18529 | Slave14 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18530 | Slave14 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18531 | Slave14 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18532 | Slave14 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18533 | Slave14 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18534 | Slave14 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18535 | Slave14 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18536 | Slave14 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18537 | Slave14 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18538 | Slave14 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18539 | Slave14 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18540 | Slave14 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18541 | Slave14 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18542 | Slave14 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18543 | Slave14 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18544 | Slave15 Outlet Port01 Over Power Critical | RW | 2 bytes | Unit:1
18545 | Slave15 Outlet Port02 Over Power Critical | RW | 2 bytes | Unit:1
18546 | Slave15 Outlet Port03 Over Power Critical | RW | 2 bytes | Unit:1
18547 | Slave15 Outlet Port04 Over Power Critical | RW | 2 bytes | Unit:1
18548 | Slave15 Outlet Port05 Over Power Critical | RW | 2 bytes | Unit:1
18549 | Slave15 Outlet Port06 Over Power Critical | RW | 2 bytes | Unit:1
18550 | Slave15 Outlet Port07 Over Power Critical | RW | 2 bytes | Unit:1
18551 | Slave15 Outlet Port08 Over Power Critical | RW | 2 bytes | Unit:1
18552 | Slave15 Outlet Port09 Over Power Critical | RW | 2 bytes | Unit:1
18553 | Slave15 Outlet Port10 Over Power Critical | RW | 2 bytes | Unit:1
18554 | Slave15 Outlet Port11 Over Power Critical | RW | 2 bytes | Unit:1
18555 | Slave15 Outlet Port12 Over Power Critical | RW | 2 bytes | Unit:1
18556 | Slave15 Outlet Port13 Over Power Critical | RW | 2 bytes | Unit:1
18557 | Slave15 Outlet Port14 Over Power Critical | RW | 2 bytes | Unit:1
18558 | Slave15 Outlet Port15 Over Power Critical | RW | 2 bytes | Unit:1
18559 | Slave15 Outlet Port16 Over Power Critical | RW | 2 bytes | Unit:1
18560 | Slave15 Outlet Port17 Over Power Critical | RW | 2 bytes | Unit:1
18561 | Slave15 Outlet Port18 Over Power Critical | RW | 2 bytes | Unit:1
18562 | Slave15 Outlet Port19 Over Power Critical | RW | 2 bytes | Unit:1
18563 | Slave15 Outlet Port20 Over Power Critical | RW | 2 bytes | Unit:1
18564 | Slave15 Outlet Port21 Over Power Critical | RW | 2 bytes | Unit:1
18565 | Slave15 Outlet Port22 Over Power Critical | RW | 2 bytes | Unit:1
18566 | Slave15 Outlet Port23 Over Power Critical | RW | 2 bytes | Unit:1
18567 | Slave15 Outlet Port24 Over Power Critical | RW | 2 bytes | Unit:1
18568 | Slave15 Outlet Port25 Over Power Critical | RW | 2 bytes | Unit:1
18569 | Slave15 Outlet Port26 Over Power Critical | RW | 2 bytes | Unit:1
18570 | Slave15 Outlet Port27 Over Power Critical | RW | 2 bytes | Unit:1
18571 | Slave15 Outlet Port28 Over Power Critical | RW | 2 bytes | Unit:1
18572 | Slave15 Outlet Port29 Over Power Critical | RW | 2 bytes | Unit:1
18573 | Slave15 Outlet Port30 Over Power Critical | RW | 2 bytes | Unit:1
18574 | Slave15 Outlet Port31 Over Power Critical | RW | 2 bytes | Unit:1
18575 | Slave15 Outlet Port32 Over Power Critical | RW | 2 bytes | Unit:1
18576 | Slave15 Outlet Port33 Over Power Critical | RW | 2 bytes | Unit:1
18577 | Slave15 Outlet Port34 Over Power Critical | RW | 2 bytes | Unit:1
18578 | Slave15 Outlet Port35 Over Power Critical | RW | 2 bytes | Unit:1
18579 | Slave15 Outlet Port36 Over Power Critical | RW | 2 bytes | Unit:1
18580 | Slave15 Outlet Port37 Over Power Critical | RW | 2 bytes | Unit:1
18581 | Slave15 Outlet Port38 Over Power Critical | RW | 2 bytes | Unit:1
18582 | Slave15 Outlet Port39 Over Power Critical | RW | 2 bytes | Unit:1
18583 | Slave15 Outlet Port40 Over Power Critical | RW | 2 bytes | Unit:1
18584 | Slave15 Outlet Port41 Over Power Critical | RW | 2 bytes | Unit:1
18585 | Slave15 Outlet Port42 Over Power Critical | RW | 2 bytes | Unit:1
18586 | Slave15 Outlet Port43 Over Power Critical | RW | 2 bytes | Unit:1
18587 | Slave15 Outlet Port44 Over Power Critical | RW | 2 bytes | Unit:1
18588 | Slave15 Outlet Port45 Over Power Critical | RW | 2 bytes | Unit:1
18589 | Slave15 Outlet Port46 Over Power Critical | RW | 2 bytes | Unit:1
18590 | Slave15 Outlet Port47 Over Power Critical | RW | 2 bytes | Unit:1
18591 | Slave15 Outlet Port48 Over Power Critical | RW | 2 bytes | Unit:1
18592 | Master Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18593 | Master Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18594 | Master Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18595 | Master Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18596 | Master Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18597 | Master Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18598 | Master Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18599 | Master Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18600 | Master Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18601 | Master Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18602 | Master Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18603 | Master Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18604 | Master Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18605 | Master Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18606 | Master Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18607 | Master Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18608 | Master Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18609 | Master Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18610 | Master Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18611 | Master Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18612 | Master Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18613 | Master Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18614 | Master Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18615 | Master Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18616 | Master Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18617 | Master Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18618 | Master Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18619 | Master Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18620 | Master Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18621 | Master Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18622 | Master Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18623 | Master Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18624 | Master Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18625 | Master Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18626 | Master Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18627 | Master Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18628 | Master Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18629 | Master Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18630 | Master Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18631 | Master Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18632 | Master Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18633 | Master Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18634 | Master Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18635 | Master Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18636 | Master Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18637 | Master Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18638 | Master Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18639 | Master Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18640 | Slave01 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18641 | Slave01 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18642 | Slave01 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18643 | Slave01 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18644 | Slave01 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18645 | Slave01 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18646 | Slave01 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18647 | Slave01 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18648 | Slave01 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18649 | Slave01 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18650 | Slave01 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18651 | Slave01 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18652 | Slave01 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18653 | Slave01 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18654 | Slave01 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18655 | Slave01 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18656 | Slave01 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18657 | Slave01 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18658 | Slave01 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18659 | Slave01 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18660 | Slave01 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18661 | Slave01 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18662 | Slave01 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18663 | Slave01 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18664 | Slave01 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18665 | Slave01 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18666 | Slave01 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18667 | Slave01 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18668 | Slave01 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18669 | Slave01 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18670 | Slave01 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18671 | Slave01 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18672 | Slave01 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18673 | Slave01 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18674 | Slave01 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18675 | Slave01 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18676 | Slave01 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18677 | Slave01 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18678 | Slave01 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18679 | Slave01 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18680 | Slave01 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18681 | Slave01 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18682 | Slave01 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18683 | Slave01 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18684 | Slave01 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18685 | Slave01 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18686 | Slave01 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18687 | Slave01 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18688 | Slave02 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18689 | Slave02 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18690 | Slave02 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18691 | Slave02 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18692 | Slave02 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18693 | Slave02 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18694 | Slave02 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18695 | Slave02 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18696 | Slave02 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18697 | Slave02 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18698 | Slave02 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18699 | Slave02 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18700 | Slave02 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18701 | Slave02 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18702 | Slave02 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18703 | Slave02 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18704 | Slave02 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18705 | Slave02 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18706 | Slave02 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18707 | Slave02 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18708 | Slave02 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18709 | Slave02 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18710 | Slave02 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18711 | Slave02 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18712 | Slave02 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18713 | Slave02 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18714 | Slave02 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18715 | Slave02 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18716 | Slave02 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18717 | Slave02 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18718 | Slave02 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18719 | Slave02 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18720 | Slave02 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18721 | Slave02 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18722 | Slave02 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18723 | Slave02 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18724 | Slave02 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18725 | Slave02 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18726 | Slave02 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18727 | Slave02 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18728 | Slave02 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18729 | Slave02 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18730 | Slave02 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18731 | Slave02 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18732 | Slave02 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18733 | Slave02 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18734 | Slave02 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18735 | Slave02 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18736 | Slave03 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18737 | Slave03 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18738 | Slave03 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18739 | Slave03 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18740 | Slave03 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18741 | Slave03 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18742 | Slave03 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18743 | Slave03 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18744 | Slave03 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18745 | Slave03 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18746 | Slave03 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18747 | Slave03 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18748 | Slave03 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18749 | Slave03 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18750 | Slave03 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18751 | Slave03 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18752 | Slave03 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18753 | Slave03 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18754 | Slave03 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18755 | Slave03 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18756 | Slave03 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18757 | Slave03 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18758 | Slave03 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18759 | Slave03 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18760 | Slave03 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18761 | Slave03 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18762 | Slave03 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18763 | Slave03 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18764 | Slave03 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18765 | Slave03 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18766 | Slave03 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18767 | Slave03 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18768 | Slave03 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18769 | Slave03 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18770 | Slave03 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18771 | Slave03 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18772 | Slave03 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18773 | Slave03 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18774 | Slave03 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18775 | Slave03 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18776 | Slave03 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18777 | Slave03 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18778 | Slave03 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18779 | Slave03 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18780 | Slave03 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18781 | Slave03 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18782 | Slave03 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18783 | Slave03 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18784 | Slave04 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18785 | Slave04 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18786 | Slave04 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18787 | Slave04 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18788 | Slave04 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18789 | Slave04 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18790 | Slave04 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18791 | Slave04 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18792 | Slave04 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18793 | Slave04 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18794 | Slave04 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18795 | Slave04 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18796 | Slave04 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18797 | Slave04 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18798 | Slave04 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18799 | Slave04 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18800 | Slave04 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18801 | Slave04 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18802 | Slave04 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18803 | Slave04 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18804 | Slave04 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18805 | Slave04 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18806 | Slave04 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18807 | Slave04 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18808 | Slave04 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18809 | Slave04 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18810 | Slave04 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18811 | Slave04 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18812 | Slave04 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18813 | Slave04 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18814 | Slave04 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18815 | Slave04 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18816 | Slave04 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18817 | Slave04 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18818 | Slave04 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18819 | Slave04 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18820 | Slave04 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18821 | Slave04 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18822 | Slave04 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18823 | Slave04 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18824 | Slave04 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18825 | Slave04 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18826 | Slave04 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18827 | Slave04 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18828 | Slave04 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18829 | Slave04 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18830 | Slave04 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18831 | Slave04 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18832 | Slave05 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18833 | Slave05 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18834 | Slave05 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18835 | Slave05 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18836 | Slave05 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18837 | Slave05 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18838 | Slave05 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18839 | Slave05 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18840 | Slave05 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18841 | Slave05 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18842 | Slave05 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18843 | Slave05 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18844 | Slave05 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18845 | Slave05 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18846 | Slave05 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18847 | Slave05 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18848 | Slave05 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18849 | Slave05 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18850 | Slave05 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18851 | Slave05 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18852 | Slave05 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18853 | Slave05 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18854 | Slave05 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18855 | Slave05 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18856 | Slave05 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18857 | Slave05 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18858 | Slave05 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18859 | Slave05 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18860 | Slave05 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18861 | Slave05 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18862 | Slave05 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18863 | Slave05 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18864 | Slave05 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18865 | Slave05 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18866 | Slave05 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18867 | Slave05 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18868 | Slave05 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18869 | Slave05 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18870 | Slave05 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18871 | Slave05 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18872 | Slave05 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18873 | Slave05 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18874 | Slave05 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18875 | Slave05 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18876 | Slave05 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18877 | Slave05 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18878 | Slave05 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18879 | Slave05 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18880 | Slave06 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18881 | Slave06 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18882 | Slave06 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18883 | Slave06 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18884 | Slave06 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18885 | Slave06 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18886 | Slave06 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18887 | Slave06 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18888 | Slave06 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18889 | Slave06 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18890 | Slave06 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18891 | Slave06 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18892 | Slave06 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18893 | Slave06 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18894 | Slave06 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18895 | Slave06 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18896 | Slave06 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18897 | Slave06 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18898 | Slave06 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18899 | Slave06 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18900 | Slave06 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18901 | Slave06 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18902 | Slave06 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18903 | Slave06 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18904 | Slave06 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18905 | Slave06 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18906 | Slave06 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18907 | Slave06 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18908 | Slave06 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18909 | Slave06 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18910 | Slave06 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18911 | Slave06 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18912 | Slave06 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18913 | Slave06 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18914 | Slave06 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18915 | Slave06 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18916 | Slave06 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18917 | Slave06 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18918 | Slave06 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18919 | Slave06 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18920 | Slave06 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18921 | Slave06 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18922 | Slave06 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18923 | Slave06 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18924 | Slave06 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18925 | Slave06 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18926 | Slave06 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18927 | Slave06 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18928 | Slave07 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18929 | Slave07 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18930 | Slave07 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18931 | Slave07 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18932 | Slave07 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18933 | Slave07 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18934 | Slave07 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18935 | Slave07 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18936 | Slave07 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18937 | Slave07 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18938 | Slave07 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18939 | Slave07 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18940 | Slave07 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18941 | Slave07 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18942 | Slave07 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18943 | Slave07 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18944 | Slave07 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18945 | Slave07 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18946 | Slave07 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18947 | Slave07 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18948 | Slave07 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18949 | Slave07 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18950 | Slave07 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18951 | Slave07 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18952 | Slave07 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18953 | Slave07 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18954 | Slave07 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18955 | Slave07 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18956 | Slave07 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18957 | Slave07 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18958 | Slave07 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18959 | Slave07 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18960 | Slave07 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18961 | Slave07 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18962 | Slave07 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18963 | Slave07 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18964 | Slave07 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18965 | Slave07 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18966 | Slave07 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18967 | Slave07 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18968 | Slave07 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18969 | Slave07 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18970 | Slave07 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18971 | Slave07 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18972 | Slave07 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18973 | Slave07 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18974 | Slave07 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18975 | Slave07 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18976 | Slave08 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18977 | Slave08 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18978 | Slave08 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18979 | Slave08 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18980 | Slave08 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18981 | Slave08 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18982 | Slave08 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18983 | Slave08 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18984 | Slave08 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18985 | Slave08 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18986 | Slave08 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18987 | Slave08 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18988 | Slave08 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18989 | Slave08 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18990 | Slave08 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18991 | Slave08 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18992 | Slave08 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18993 | Slave08 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18994 | Slave08 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18995 | Slave08 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18996 | Slave08 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18997 | Slave08 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18998 | Slave08 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
18999 | Slave08 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19000 | Slave08 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19001 | Slave08 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19002 | Slave08 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19003 | Slave08 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19004 | Slave08 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19005 | Slave08 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19006 | Slave08 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19007 | Slave08 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19008 | Slave08 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19009 | Slave08 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19010 | Slave08 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19011 | Slave08 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19012 | Slave08 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19013 | Slave08 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19014 | Slave08 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19015 | Slave08 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19016 | Slave08 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19017 | Slave08 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19018 | Slave08 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19019 | Slave08 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19020 | Slave08 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19021 | Slave08 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19022 | Slave08 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19023 | Slave08 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19024 | Slave09 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19025 | Slave09 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19026 | Slave09 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19027 | Slave09 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19028 | Slave09 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19029 | Slave09 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19030 | Slave09 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19031 | Slave09 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19032 | Slave09 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19033 | Slave09 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19034 | Slave09 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19035 | Slave09 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19036 | Slave09 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19037 | Slave09 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19038 | Slave09 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19039 | Slave09 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19040 | Slave09 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19041 | Slave09 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19042 | Slave09 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19043 | Slave09 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19044 | Slave09 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19045 | Slave09 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19046 | Slave09 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19047 | Slave09 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19048 | Slave09 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19049 | Slave09 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19050 | Slave09 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19051 | Slave09 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19052 | Slave09 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19053 | Slave09 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19054 | Slave09 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19055 | Slave09 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19056 | Slave09 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19057 | Slave09 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19058 | Slave09 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19059 | Slave09 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19060 | Slave09 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19061 | Slave09 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19062 | Slave09 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19063 | Slave09 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19064 | Slave09 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19065 | Slave09 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19066 | Slave09 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19067 | Slave09 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19068 | Slave09 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19069 | Slave09 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19070 | Slave09 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19071 | Slave09 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19072 | Slave10 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19073 | Slave10 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19074 | Slave10 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19075 | Slave10 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19076 | Slave10 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19077 | Slave10 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19078 | Slave10 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19079 | Slave10 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19080 | Slave10 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19081 | Slave10 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19082 | Slave10 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19083 | Slave10 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19084 | Slave10 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19085 | Slave10 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19086 | Slave10 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19087 | Slave10 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19088 | Slave10 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19089 | Slave10 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19090 | Slave10 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19091 | Slave10 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19092 | Slave10 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19093 | Slave10 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19094 | Slave10 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19095 | Slave10 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19096 | Slave10 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19097 | Slave10 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19098 | Slave10 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19099 | Slave10 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19100 | Slave10 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19101 | Slave10 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19102 | Slave10 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19103 | Slave10 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19104 | Slave10 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19105 | Slave10 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19106 | Slave10 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19107 | Slave10 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19108 | Slave10 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19109 | Slave10 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19110 | Slave10 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19111 | Slave10 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19112 | Slave10 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19113 | Slave10 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19114 | Slave10 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19115 | Slave10 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19116 | Slave10 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19117 | Slave10 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19118 | Slave10 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19119 | Slave10 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19120 | Slave11 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19121 | Slave11 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19122 | Slave11 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19123 | Slave11 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19124 | Slave11 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19125 | Slave11 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19126 | Slave11 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19127 | Slave11 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19128 | Slave11 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19129 | Slave11 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19130 | Slave11 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19131 | Slave11 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19132 | Slave11 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19133 | Slave11 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19134 | Slave11 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19135 | Slave11 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19136 | Slave11 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19137 | Slave11 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19138 | Slave11 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19139 | Slave11 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19140 | Slave11 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19141 | Slave11 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19142 | Slave11 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19143 | Slave11 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19144 | Slave11 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19145 | Slave11 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19146 | Slave11 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19147 | Slave11 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19148 | Slave11 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19149 | Slave11 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19150 | Slave11 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19151 | Slave11 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19152 | Slave11 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19153 | Slave11 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19154 | Slave11 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19155 | Slave11 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19156 | Slave11 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19157 | Slave11 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19158 | Slave11 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19159 | Slave11 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19160 | Slave11 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19161 | Slave11 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19162 | Slave11 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19163 | Slave11 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19164 | Slave11 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19165 | Slave11 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19166 | Slave11 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19167 | Slave11 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19168 | Slave12 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19169 | Slave12 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19170 | Slave12 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19171 | Slave12 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19172 | Slave12 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19173 | Slave12 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19174 | Slave12 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19175 | Slave12 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19176 | Slave12 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19177 | Slave12 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19178 | Slave12 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19179 | Slave12 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19180 | Slave12 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19181 | Slave12 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19182 | Slave12 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19183 | Slave12 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19184 | Slave12 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19185 | Slave12 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19186 | Slave12 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19187 | Slave12 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19188 | Slave12 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19189 | Slave12 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19190 | Slave12 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19191 | Slave12 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19192 | Slave12 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19193 | Slave12 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19194 | Slave12 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19195 | Slave12 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19196 | Slave12 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19197 | Slave12 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19198 | Slave12 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19199 | Slave12 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19200 | Slave12 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19201 | Slave12 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19202 | Slave12 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19203 | Slave12 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19204 | Slave12 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19205 | Slave12 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19206 | Slave12 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19207 | Slave12 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19208 | Slave12 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19209 | Slave12 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19210 | Slave12 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19211 | Slave12 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19212 | Slave12 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19213 | Slave12 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19214 | Slave12 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19215 | Slave12 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19216 | Slave13 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19217 | Slave13 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19218 | Slave13 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19219 | Slave13 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19220 | Slave13 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19221 | Slave13 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19222 | Slave13 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19223 | Slave13 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19224 | Slave13 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19225 | Slave13 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19226 | Slave13 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19227 | Slave13 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19228 | Slave13 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19229 | Slave13 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19230 | Slave13 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19231 | Slave13 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19232 | Slave13 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19233 | Slave13 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19234 | Slave13 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19235 | Slave13 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19236 | Slave13 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19237 | Slave13 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19238 | Slave13 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19239 | Slave13 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19240 | Slave13 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19241 | Slave13 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19242 | Slave13 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19243 | Slave13 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19244 | Slave13 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19245 | Slave13 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19246 | Slave13 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19247 | Slave13 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19248 | Slave13 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19249 | Slave13 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19250 | Slave13 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19251 | Slave13 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19252 | Slave13 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19253 | Slave13 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19254 | Slave13 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19255 | Slave13 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19256 | Slave13 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19257 | Slave13 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19258 | Slave13 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19259 | Slave13 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19260 | Slave13 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19261 | Slave13 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19262 | Slave13 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19263 | Slave13 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19264 | Slave14 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19265 | Slave14 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19266 | Slave14 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19267 | Slave14 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19268 | Slave14 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19269 | Slave14 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19270 | Slave14 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19271 | Slave14 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19272 | Slave14 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19273 | Slave14 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19274 | Slave14 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19275 | Slave14 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19276 | Slave14 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19277 | Slave14 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19278 | Slave14 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19279 | Slave14 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19280 | Slave14 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19281 | Slave14 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19282 | Slave14 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19283 | Slave14 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19284 | Slave14 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19285 | Slave14 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19286 | Slave14 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19287 | Slave14 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19288 | Slave14 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19289 | Slave14 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19290 | Slave14 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19291 | Slave14 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19292 | Slave14 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19293 | Slave14 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19294 | Slave14 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19295 | Slave14 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19296 | Slave14 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19297 | Slave14 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19298 | Slave14 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19299 | Slave14 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19300 | Slave14 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19301 | Slave14 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19302 | Slave14 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19303 | Slave14 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19304 | Slave14 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19305 | Slave14 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19306 | Slave14 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19307 | Slave14 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19308 | Slave14 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19309 | Slave14 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19310 | Slave14 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19311 | Slave14 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19312 | Slave15 Outlet Port01 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19313 | Slave15 Outlet Port02 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19314 | Slave15 Outlet Port03 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19315 | Slave15 Outlet Port04 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19316 | Slave15 Outlet Port05 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19317 | Slave15 Outlet Port06 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19318 | Slave15 Outlet Port07 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19319 | Slave15 Outlet Port08 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19320 | Slave15 Outlet Port09 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19321 | Slave15 Outlet Port10 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19322 | Slave15 Outlet Port11 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19323 | Slave15 Outlet Port12 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19324 | Slave15 Outlet Port13 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19325 | Slave15 Outlet Port14 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19326 | Slave15 Outlet Port15 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19327 | Slave15 Outlet Port16 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19328 | Slave15 Outlet Port17 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19329 | Slave15 Outlet Port18 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19330 | Slave15 Outlet Port19 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19331 | Slave15 Outlet Port20 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19332 | Slave15 Outlet Port21 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19333 | Slave15 Outlet Port22 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19334 | Slave15 Outlet Port23 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19335 | Slave15 Outlet Port24 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19336 | Slave15 Outlet Port25 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19337 | Slave15 Outlet Port26 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19338 | Slave15 Outlet Port27 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19339 | Slave15 Outlet Port28 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19340 | Slave15 Outlet Port29 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19341 | Slave15 Outlet Port30 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19342 | Slave15 Outlet Port31 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19343 | Slave15 Outlet Port32 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19344 | Slave15 Outlet Port33 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19345 | Slave15 Outlet Port34 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19346 | Slave15 Outlet Port35 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19347 | Slave15 Outlet Port36 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19348 | Slave15 Outlet Port37 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19349 | Slave15 Outlet Port38 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19350 | Slave15 Outlet Port39 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19351 | Slave15 Outlet Port40 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19352 | Slave15 Outlet Port41 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19353 | Slave15 Outlet Port42 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19354 | Slave15 Outlet Port43 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19355 | Slave15 Outlet Port44 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19356 | Slave15 Outlet Port45 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19357 | Slave15 Outlet Port46 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19358 | Slave15 Outlet Port47 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19359 | Slave15 Outlet Port48 Relay Control | RW | 2 bytes | 0:Nothing; 1:ImmOn; 2:DelayOn; 3:ImmOff; 4:DelayOff; 5:Cycle; 6:DelayCycle
19360 | Master EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19361 | Master EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19362 | Master EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19363 | Master EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19364 | Master EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19365 | Master EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19366 | Master EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19367 | Master EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19368 | Slave01 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19369 | Slave01 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19370 | Slave01 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19371 | Slave01 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19372 | Slave01 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19373 | Slave01 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19374 | Slave01 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19375 | Slave01 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19376 | Slave02 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19377 | Slave02 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19378 | Slave02 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19379 | Slave02 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19380 | Slave02 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19381 | Slave02 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19382 | Slave02 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19383 | Slave02 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19384 | Slave03 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19385 | Slave03 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19386 | Slave03 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19387 | Slave03 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19388 | Slave03 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19389 | Slave03 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19390 | Slave03 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19391 | Slave03 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19392 | Slave04 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19393 | Slave04 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19394 | Slave04 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19395 | Slave04 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19396 | Slave04 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19397 | Slave04 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19398 | Slave04 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19399 | Slave04 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19400 | Slave05 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19401 | Slave05 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19402 | Slave05 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19403 | Slave05 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19404 | Slave05 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19405 | Slave05 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19406 | Slave05 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19407 | Slave05 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19408 | Slave06 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19409 | Slave06 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19410 | Slave06 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19411 | Slave06 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19412 | Slave06 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19413 | Slave06 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19414 | Slave06 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19415 | Slave06 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19416 | Slave07 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19417 | Slave07 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19418 | Slave07 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19419 | Slave07 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19420 | Slave07 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19421 | Slave07 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19422 | Slave07 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19423 | Slave07 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19424 | Slave08 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19425 | Slave08 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19426 | Slave08 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19427 | Slave08 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19428 | Slave08 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19429 | Slave08 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19430 | Slave08 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19431 | Slave08 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19432 | Slave09 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19433 | Slave09 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19434 | Slave09 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19435 | Slave09 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19436 | Slave09 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19437 | Slave09 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19438 | Slave09 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19439 | Slave09 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19440 | Slave10 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19441 | Slave10 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19442 | Slave10 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19443 | Slave10 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19444 | Slave10 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19445 | Slave10 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19446 | Slave10 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19447 | Slave10 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19448 | Slave11 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19449 | Slave11 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19450 | Slave11 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19451 | Slave11 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19452 | Slave11 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19453 | Slave11 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19454 | Slave11 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19455 | Slave11 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19456 | Slave12 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19457 | Slave12 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19458 | Slave12 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19459 | Slave12 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19460 | Slave12 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19461 | Slave12 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19462 | Slave12 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19463 | Slave12 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19464 | Slave13 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19465 | Slave13 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19466 | Slave13 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19467 | Slave13 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19468 | Slave13 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19469 | Slave13 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19470 | Slave13 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19471 | Slave13 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19472 | Slave14 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19473 | Slave14 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19474 | Slave14 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19475 | Slave14 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19476 | Slave14 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19477 | Slave14 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19478 | Slave14 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19479 | Slave14 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19480 | Slave15 EMD-1 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19481 | Slave15 EMD-2 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19482 | Slave15 EMD-3 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19483 | Slave15 EMD-4 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19484 | Slave15 EMD-5 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19485 | Slave15 EMD-6 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19486 | Slave15 EMD-7 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19487 | Slave15 EMD-8 Enable Temperature High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19488 | Master EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19489 | Master EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19490 | Master EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19491 | Master EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19492 | Master EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19493 | Master EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19494 | Master EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19495 | Master EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19496 | Slave01 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19497 | Slave01 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19498 | Slave01 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19499 | Slave01 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19500 | Slave01 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19501 | Slave01 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19502 | Slave01 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19503 | Slave01 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19504 | Slave02 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19505 | Slave02 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19506 | Slave02 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19507 | Slave02 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19508 | Slave02 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19509 | Slave02 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19510 | Slave02 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19511 | Slave02 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19512 | Slave03 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19513 | Slave03 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19514 | Slave03 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19515 | Slave03 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19516 | Slave03 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19517 | Slave03 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19518 | Slave03 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19519 | Slave03 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19520 | Slave04 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19521 | Slave04 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19522 | Slave04 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19523 | Slave04 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19524 | Slave04 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19525 | Slave04 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19526 | Slave04 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19527 | Slave04 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19528 | Slave05 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19529 | Slave05 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19530 | Slave05 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19531 | Slave05 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19532 | Slave05 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19533 | Slave05 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19534 | Slave05 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19535 | Slave05 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19536 | Slave06 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19537 | Slave06 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19538 | Slave06 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19539 | Slave06 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19540 | Slave06 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19541 | Slave06 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19542 | Slave06 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19543 | Slave06 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19544 | Slave07 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19545 | Slave07 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19546 | Slave07 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19547 | Slave07 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19548 | Slave07 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19549 | Slave07 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19550 | Slave07 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19551 | Slave07 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19552 | Slave08 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19553 | Slave08 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19554 | Slave08 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19555 | Slave08 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19556 | Slave08 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19557 | Slave08 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19558 | Slave08 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19559 | Slave08 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19560 | Slave09 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19561 | Slave09 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19562 | Slave09 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19563 | Slave09 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19564 | Slave09 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19565 | Slave09 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19566 | Slave09 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19567 | Slave09 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19568 | Slave10 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19569 | Slave10 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19570 | Slave10 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19571 | Slave10 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19572 | Slave10 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19573 | Slave10 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19574 | Slave10 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19575 | Slave10 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19576 | Slave11 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19577 | Slave11 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19578 | Slave11 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19579 | Slave11 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19580 | Slave11 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19581 | Slave11 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19582 | Slave11 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19583 | Slave11 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19584 | Slave12 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19585 | Slave12 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19586 | Slave12 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19587 | Slave12 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19588 | Slave12 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19589 | Slave12 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19590 | Slave12 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19591 | Slave12 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19592 | Slave13 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19593 | Slave13 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19594 | Slave13 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19595 | Slave13 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19596 | Slave13 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19597 | Slave13 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19598 | Slave13 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19599 | Slave13 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19600 | Slave14 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19601 | Slave14 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19602 | Slave14 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19603 | Slave14 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19604 | Slave14 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19605 | Slave14 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19606 | Slave14 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19607 | Slave14 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19608 | Slave15 EMD-1 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19609 | Slave15 EMD-2 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19610 | Slave15 EMD-3 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19611 | Slave15 EMD-4 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19612 | Slave15 EMD-5 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19613 | Slave15 EMD-6 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19614 | Slave15 EMD-7 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19615 | Slave15 EMD-8 Enable Temperature Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19616 | Master EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19617 | Master EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19618 | Master EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19619 | Master EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19620 | Master EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19621 | Master EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19622 | Master EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19623 | Master EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19624 | Slave01 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19625 | Slave01 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19626 | Slave01 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19627 | Slave01 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19628 | Slave01 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19629 | Slave01 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19630 | Slave01 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19631 | Slave01 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19632 | Slave02 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19633 | Slave02 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19634 | Slave02 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19635 | Slave02 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19636 | Slave02 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19637 | Slave02 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19638 | Slave02 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19639 | Slave02 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19640 | Slave03 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19641 | Slave03 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19642 | Slave03 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19643 | Slave03 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19644 | Slave03 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19645 | Slave03 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19646 | Slave03 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19647 | Slave03 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19648 | Slave04 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19649 | Slave04 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19650 | Slave04 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19651 | Slave04 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19652 | Slave04 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19653 | Slave04 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19654 | Slave04 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19655 | Slave04 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19656 | Slave05 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19657 | Slave05 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19658 | Slave05 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19659 | Slave05 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19660 | Slave05 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19661 | Slave05 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19662 | Slave05 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19663 | Slave05 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19664 | Slave06 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19665 | Slave06 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19666 | Slave06 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19667 | Slave06 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19668 | Slave06 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19669 | Slave06 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19670 | Slave06 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19671 | Slave06 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19672 | Slave07 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19673 | Slave07 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19674 | Slave07 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19675 | Slave07 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19676 | Slave07 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19677 | Slave07 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19678 | Slave07 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19679 | Slave07 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19680 | Slave08 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19681 | Slave08 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19682 | Slave08 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19683 | Slave08 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19684 | Slave08 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19685 | Slave08 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19686 | Slave08 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19687 | Slave08 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19688 | Slave09 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19689 | Slave09 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19690 | Slave09 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19691 | Slave09 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19692 | Slave09 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19693 | Slave09 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19694 | Slave09 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19695 | Slave09 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19696 | Slave10 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19697 | Slave10 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19698 | Slave10 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19699 | Slave10 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19700 | Slave10 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19701 | Slave10 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19702 | Slave10 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19703 | Slave10 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19704 | Slave11 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19705 | Slave11 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19706 | Slave11 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19707 | Slave11 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19708 | Slave11 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19709 | Slave11 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19710 | Slave11 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19711 | Slave11 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19712 | Slave12 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19713 | Slave12 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19714 | Slave12 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19715 | Slave12 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19716 | Slave12 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19717 | Slave12 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19718 | Slave12 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19719 | Slave12 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19720 | Slave13 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19721 | Slave13 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19722 | Slave13 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19723 | Slave13 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19724 | Slave13 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19725 | Slave13 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19726 | Slave13 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19727 | Slave13 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19728 | Slave14 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19729 | Slave14 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19730 | Slave14 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19731 | Slave14 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19732 | Slave14 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19733 | Slave14 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19734 | Slave14 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19735 | Slave14 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19736 | Slave15 EMD-1 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19737 | Slave15 EMD-2 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19738 | Slave15 EMD-3 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19739 | Slave15 EMD-4 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19740 | Slave15 EMD-5 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19741 | Slave15 EMD-6 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19742 | Slave15 EMD-7 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19743 | Slave15 EMD-8 Enable Temperature High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19744 | Master EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19745 | Master EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19746 | Master EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19747 | Master EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19748 | Master EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19749 | Master EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19750 | Master EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19751 | Master EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19752 | Slave01 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19753 | Slave01 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19754 | Slave01 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19755 | Slave01 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19756 | Slave01 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19757 | Slave01 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19758 | Slave01 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19759 | Slave01 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19760 | Slave02 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19761 | Slave02 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19762 | Slave02 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19763 | Slave02 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19764 | Slave02 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19765 | Slave02 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19766 | Slave02 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19767 | Slave02 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19768 | Slave03 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19769 | Slave03 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19770 | Slave03 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19771 | Slave03 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19772 | Slave03 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19773 | Slave03 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19774 | Slave03 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19775 | Slave03 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19776 | Slave04 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19777 | Slave04 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19778 | Slave04 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19779 | Slave04 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19780 | Slave04 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19781 | Slave04 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19782 | Slave04 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19783 | Slave04 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19784 | Slave05 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19785 | Slave05 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19786 | Slave05 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19787 | Slave05 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19788 | Slave05 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19789 | Slave05 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19790 | Slave05 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19791 | Slave05 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19792 | Slave06 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19793 | Slave06 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19794 | Slave06 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19795 | Slave06 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19796 | Slave06 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19797 | Slave06 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19798 | Slave06 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19799 | Slave06 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19800 | Slave07 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19801 | Slave07 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19802 | Slave07 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19803 | Slave07 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19804 | Slave07 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19805 | Slave07 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19806 | Slave07 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19807 | Slave07 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19808 | Slave08 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19809 | Slave08 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19810 | Slave08 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19811 | Slave08 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19812 | Slave08 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19813 | Slave08 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19814 | Slave08 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19815 | Slave08 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19816 | Slave09 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19817 | Slave09 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19818 | Slave09 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19819 | Slave09 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19820 | Slave09 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19821 | Slave09 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19822 | Slave09 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19823 | Slave09 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19824 | Slave10 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19825 | Slave10 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19826 | Slave10 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19827 | Slave10 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19828 | Slave10 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19829 | Slave10 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19830 | Slave10 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19831 | Slave10 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19832 | Slave11 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19833 | Slave11 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19834 | Slave11 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19835 | Slave11 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19836 | Slave11 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19837 | Slave11 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19838 | Slave11 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19839 | Slave11 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19840 | Slave12 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19841 | Slave12 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19842 | Slave12 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19843 | Slave12 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19844 | Slave12 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19845 | Slave12 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19846 | Slave12 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19847 | Slave12 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19848 | Slave13 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19849 | Slave13 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19850 | Slave13 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19851 | Slave13 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19852 | Slave13 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19853 | Slave13 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19854 | Slave13 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19855 | Slave13 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19856 | Slave14 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19857 | Slave14 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19858 | Slave14 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19859 | Slave14 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19860 | Slave14 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19861 | Slave14 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19862 | Slave14 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19863 | Slave14 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19864 | Slave15 EMD-1 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19865 | Slave15 EMD-2 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19866 | Slave15 EMD-3 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19867 | Slave15 EMD-4 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19868 | Slave15 EMD-5 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19869 | Slave15 EMD-6 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19870 | Slave15 EMD-7 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19871 | Slave15 EMD-8 Enable Temperature Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
19872 | Master EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19873 | Master EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19874 | Master EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19875 | Master EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19876 | Master EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19877 | Master EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19878 | Master EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19879 | Master EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19880 | Slave01 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19881 | Slave01 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19882 | Slave01 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19883 | Slave01 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19884 | Slave01 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19885 | Slave01 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19886 | Slave01 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19887 | Slave01 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19888 | Slave02 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19889 | Slave02 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19890 | Slave02 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19891 | Slave02 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19892 | Slave02 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19893 | Slave02 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19894 | Slave02 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19895 | Slave02 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19896 | Slave03 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19897 | Slave03 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19898 | Slave03 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19899 | Slave03 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19900 | Slave03 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19901 | Slave03 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19902 | Slave03 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19903 | Slave03 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19904 | Slave04 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19905 | Slave04 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19906 | Slave04 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19907 | Slave04 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19908 | Slave04 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19909 | Slave04 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19910 | Slave04 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19911 | Slave04 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19912 | Slave05 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19913 | Slave05 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19914 | Slave05 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19915 | Slave05 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19916 | Slave05 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19917 | Slave05 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19918 | Slave05 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19919 | Slave05 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19920 | Slave06 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19921 | Slave06 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19922 | Slave06 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19923 | Slave06 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19924 | Slave06 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19925 | Slave06 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19926 | Slave06 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19927 | Slave06 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19928 | Slave07 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19929 | Slave07 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19930 | Slave07 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19931 | Slave07 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19932 | Slave07 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19933 | Slave07 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19934 | Slave07 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19935 | Slave07 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19936 | Slave08 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19937 | Slave08 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19938 | Slave08 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19939 | Slave08 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19940 | Slave08 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19941 | Slave08 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19942 | Slave08 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19943 | Slave08 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19944 | Slave09 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19945 | Slave09 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19946 | Slave09 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19947 | Slave09 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19948 | Slave09 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19949 | Slave09 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19950 | Slave09 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19951 | Slave09 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19952 | Slave10 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19953 | Slave10 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19954 | Slave10 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19955 | Slave10 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19956 | Slave10 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19957 | Slave10 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19958 | Slave10 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19959 | Slave10 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19960 | Slave11 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19961 | Slave11 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19962 | Slave11 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19963 | Slave11 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19964 | Slave11 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19965 | Slave11 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19966 | Slave11 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19967 | Slave11 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19968 | Slave12 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19969 | Slave12 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19970 | Slave12 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19971 | Slave12 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19972 | Slave12 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19973 | Slave12 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19974 | Slave12 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19975 | Slave12 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19976 | Slave13 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19977 | Slave13 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19978 | Slave13 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19979 | Slave13 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19980 | Slave13 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19981 | Slave13 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19982 | Slave13 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19983 | Slave13 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19984 | Slave14 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19985 | Slave14 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19986 | Slave14 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19987 | Slave14 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19988 | Slave14 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19989 | Slave14 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19990 | Slave14 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19991 | Slave14 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19992 | Slave15 EMD-1 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19993 | Slave15 EMD-2 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19994 | Slave15 EMD-3 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19995 | Slave15 EMD-4 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19996 | Slave15 EMD-5 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19997 | Slave15 EMD-6 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19998 | Slave15 EMD-7 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
19999 | Slave15 EMD-8 Temperature High Warining Threshold | RW | 2 bytes | Unit:0.1C
20000 | Master EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20001 | Master EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20002 | Master EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20003 | Master EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20004 | Master EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20005 | Master EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20006 | Master EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20007 | Master EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20008 | Slave01 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20009 | Slave01 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20010 | Slave01 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20011 | Slave01 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20012 | Slave01 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20013 | Slave01 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20014 | Slave01 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20015 | Slave01 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20016 | Slave02 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20017 | Slave02 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20018 | Slave02 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20019 | Slave02 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20020 | Slave02 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20021 | Slave02 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20022 | Slave02 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20023 | Slave02 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20024 | Slave03 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20025 | Slave03 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20026 | Slave03 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20027 | Slave03 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20028 | Slave03 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20029 | Slave03 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20030 | Slave03 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20031 | Slave03 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20032 | Slave04 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20033 | Slave04 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20034 | Slave04 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20035 | Slave04 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20036 | Slave04 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20037 | Slave04 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20038 | Slave04 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20039 | Slave04 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20040 | Slave05 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20041 | Slave05 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20042 | Slave05 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20043 | Slave05 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20044 | Slave05 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20045 | Slave05 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20046 | Slave05 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20047 | Slave05 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20048 | Slave06 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20049 | Slave06 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20050 | Slave06 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20051 | Slave06 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20052 | Slave06 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20053 | Slave06 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20054 | Slave06 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20055 | Slave06 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20056 | Slave07 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20057 | Slave07 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20058 | Slave07 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20059 | Slave07 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20060 | Slave07 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20061 | Slave07 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20062 | Slave07 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20063 | Slave07 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20064 | Slave08 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20065 | Slave08 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20066 | Slave08 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20067 | Slave08 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20068 | Slave08 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20069 | Slave08 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20070 | Slave08 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20071 | Slave08 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20072 | Slave09 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20073 | Slave09 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20074 | Slave09 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20075 | Slave09 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20076 | Slave09 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20077 | Slave09 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20078 | Slave09 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20079 | Slave09 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20080 | Slave10 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20081 | Slave10 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20082 | Slave10 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20083 | Slave10 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20084 | Slave10 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20085 | Slave10 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20086 | Slave10 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20087 | Slave10 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20088 | Slave11 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20089 | Slave11 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20090 | Slave11 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20091 | Slave11 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20092 | Slave11 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20093 | Slave11 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20094 | Slave11 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20095 | Slave11 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20096 | Slave12 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20097 | Slave12 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20098 | Slave12 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20099 | Slave12 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20100 | Slave12 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20101 | Slave12 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20102 | Slave12 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20103 | Slave12 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20104 | Slave13 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20105 | Slave13 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20106 | Slave13 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20107 | Slave13 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20108 | Slave13 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20109 | Slave13 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20110 | Slave13 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20111 | Slave13 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20112 | Slave14 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20113 | Slave14 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20114 | Slave14 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20115 | Slave14 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20116 | Slave14 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20117 | Slave14 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20118 | Slave14 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20119 | Slave14 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20120 | Slave15 EMD-1 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20121 | Slave15 EMD-2 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20122 | Slave15 EMD-3 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20123 | Slave15 EMD-4 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20124 | Slave15 EMD-5 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20125 | Slave15 EMD-6 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20126 | Slave15 EMD-7 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20127 | Slave15 EMD-8 Temperature Low Warining Threshold | RW | 2 bytes | Unit:0.1C
20128 | Master EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20129 | Master EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20130 | Master EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20131 | Master EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20132 | Master EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20133 | Master EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20134 | Master EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20135 | Master EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20136 | Slave01 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20137 | Slave01 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20138 | Slave01 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20139 | Slave01 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20140 | Slave01 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20141 | Slave01 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20142 | Slave01 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20143 | Slave01 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20144 | Slave02 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20145 | Slave02 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20146 | Slave02 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20147 | Slave02 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20148 | Slave02 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20149 | Slave02 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20150 | Slave02 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20151 | Slave02 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20152 | Slave03 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20153 | Slave03 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20154 | Slave03 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20155 | Slave03 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20156 | Slave03 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20157 | Slave03 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20158 | Slave03 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20159 | Slave03 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20160 | Slave04 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20161 | Slave04 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20162 | Slave04 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20163 | Slave04 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20164 | Slave04 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20165 | Slave04 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20166 | Slave04 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20167 | Slave04 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20168 | Slave05 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20169 | Slave05 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20170 | Slave05 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20171 | Slave05 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20172 | Slave05 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20173 | Slave05 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20174 | Slave05 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20175 | Slave05 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20176 | Slave06 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20177 | Slave06 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20178 | Slave06 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20179 | Slave06 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20180 | Slave06 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20181 | Slave06 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20182 | Slave06 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20183 | Slave06 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20184 | Slave07 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20185 | Slave07 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20186 | Slave07 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20187 | Slave07 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20188 | Slave07 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20189 | Slave07 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20190 | Slave07 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20191 | Slave07 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20192 | Slave08 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20193 | Slave08 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20194 | Slave08 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20195 | Slave08 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20196 | Slave08 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20197 | Slave08 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20198 | Slave08 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20199 | Slave08 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20200 | Slave09 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20201 | Slave09 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20202 | Slave09 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20203 | Slave09 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20204 | Slave09 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20205 | Slave09 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20206 | Slave09 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20207 | Slave09 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20208 | Slave10 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20209 | Slave10 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20210 | Slave10 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20211 | Slave10 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20212 | Slave10 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20213 | Slave10 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20214 | Slave10 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20215 | Slave10 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20216 | Slave11 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20217 | Slave11 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20218 | Slave11 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20219 | Slave11 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20220 | Slave11 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20221 | Slave11 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20222 | Slave11 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20223 | Slave11 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20224 | Slave12 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20225 | Slave12 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20226 | Slave12 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20227 | Slave12 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20228 | Slave12 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20229 | Slave12 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20230 | Slave12 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20231 | Slave12 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20232 | Slave13 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20233 | Slave13 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20234 | Slave13 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20235 | Slave13 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20236 | Slave13 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20237 | Slave13 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20238 | Slave13 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20239 | Slave13 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20240 | Slave14 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20241 | Slave14 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20242 | Slave14 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20243 | Slave14 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20244 | Slave14 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20245 | Slave14 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20246 | Slave14 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20247 | Slave14 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20248 | Slave15 EMD-1 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20249 | Slave15 EMD-2 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20250 | Slave15 EMD-3 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20251 | Slave15 EMD-4 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20252 | Slave15 EMD-5 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20253 | Slave15 EMD-6 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20254 | Slave15 EMD-7 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20255 | Slave15 EMD-8 Temperature High Critical Threshold | RW | 2 bytes | Unit:0.1C
20256 | Master EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20257 | Master EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20258 | Master EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20259 | Master EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20260 | Master EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20261 | Master EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20262 | Master EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20263 | Master EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20264 | Slave01 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20265 | Slave01 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20266 | Slave01 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20267 | Slave01 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20268 | Slave01 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20269 | Slave01 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20270 | Slave01 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20271 | Slave01 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20272 | Slave02 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20273 | Slave02 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20274 | Slave02 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20275 | Slave02 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20276 | Slave02 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20277 | Slave02 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20278 | Slave02 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20279 | Slave02 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20280 | Slave03 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20281 | Slave03 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20282 | Slave03 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20283 | Slave03 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20284 | Slave03 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20285 | Slave03 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20286 | Slave03 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20287 | Slave03 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20288 | Slave04 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20289 | Slave04 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20290 | Slave04 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20291 | Slave04 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20292 | Slave04 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20293 | Slave04 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20294 | Slave04 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20295 | Slave04 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20296 | Slave05 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20297 | Slave05 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20298 | Slave05 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20299 | Slave05 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20300 | Slave05 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20301 | Slave05 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20302 | Slave05 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20303 | Slave05 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20304 | Slave06 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20305 | Slave06 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20306 | Slave06 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20307 | Slave06 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20308 | Slave06 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20309 | Slave06 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20310 | Slave06 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20311 | Slave06 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20312 | Slave07 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20313 | Slave07 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20314 | Slave07 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20315 | Slave07 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20316 | Slave07 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20317 | Slave07 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20318 | Slave07 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20319 | Slave07 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20320 | Slave08 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20321 | Slave08 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20322 | Slave08 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20323 | Slave08 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20324 | Slave08 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20325 | Slave08 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20326 | Slave08 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20327 | Slave08 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20328 | Slave09 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20329 | Slave09 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20330 | Slave09 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20331 | Slave09 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20332 | Slave09 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20333 | Slave09 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20334 | Slave09 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20335 | Slave09 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20336 | Slave10 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20337 | Slave10 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20338 | Slave10 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20339 | Slave10 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20340 | Slave10 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20341 | Slave10 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20342 | Slave10 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20343 | Slave10 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20344 | Slave11 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20345 | Slave11 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20346 | Slave11 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20347 | Slave11 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20348 | Slave11 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20349 | Slave11 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20350 | Slave11 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20351 | Slave11 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20352 | Slave12 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20353 | Slave12 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20354 | Slave12 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20355 | Slave12 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20356 | Slave12 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20357 | Slave12 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20358 | Slave12 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20359 | Slave12 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20360 | Slave13 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20361 | Slave13 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20362 | Slave13 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20363 | Slave13 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20364 | Slave13 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20365 | Slave13 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20366 | Slave13 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20367 | Slave13 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20368 | Slave14 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20369 | Slave14 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20370 | Slave14 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20371 | Slave14 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20372 | Slave14 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20373 | Slave14 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20374 | Slave14 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20375 | Slave14 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20376 | Slave15 EMD-1 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20377 | Slave15 EMD-2 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20378 | Slave15 EMD-3 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20379 | Slave15 EMD-4 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20380 | Slave15 EMD-5 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20381 | Slave15 EMD-6 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20382 | Slave15 EMD-7 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20383 | Slave15 EMD-8 Temperature Low Critical Threshold | RW | 2 bytes | Unit:0.1C
20384 | Master EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20385 | Master EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20386 | Master EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20387 | Master EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20388 | Master EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20389 | Master EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20390 | Master EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20391 | Master EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20392 | Slave01 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20393 | Slave01 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20394 | Slave01 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20395 | Slave01 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20396 | Slave01 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20397 | Slave01 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20398 | Slave01 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20399 | Slave01 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20400 | Slave02 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20401 | Slave02 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20402 | Slave02 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20403 | Slave02 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20404 | Slave02 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20405 | Slave02 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20406 | Slave02 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20407 | Slave02 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20408 | Slave03 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20409 | Slave03 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20410 | Slave03 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20411 | Slave03 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20412 | Slave03 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20413 | Slave03 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20414 | Slave03 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20415 | Slave03 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20416 | Slave04 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20417 | Slave04 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20418 | Slave04 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20419 | Slave04 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20420 | Slave04 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20421 | Slave04 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20422 | Slave04 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20423 | Slave04 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20424 | Slave05 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20425 | Slave05 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20426 | Slave05 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20427 | Slave05 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20428 | Slave05 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20429 | Slave05 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20430 | Slave05 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20431 | Slave05 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20432 | Slave06 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20433 | Slave06 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20434 | Slave06 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20435 | Slave06 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20436 | Slave06 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20437 | Slave06 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20438 | Slave06 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20439 | Slave06 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20440 | Slave07 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20441 | Slave07 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20442 | Slave07 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20443 | Slave07 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20444 | Slave07 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20445 | Slave07 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20446 | Slave07 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20447 | Slave07 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20448 | Slave08 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20449 | Slave08 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20450 | Slave08 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20451 | Slave08 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20452 | Slave08 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20453 | Slave08 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20454 | Slave08 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20455 | Slave08 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20456 | Slave09 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20457 | Slave09 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20458 | Slave09 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20459 | Slave09 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20460 | Slave09 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20461 | Slave09 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20462 | Slave09 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20463 | Slave09 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20464 | Slave10 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20465 | Slave10 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20466 | Slave10 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20467 | Slave10 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20468 | Slave10 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20469 | Slave10 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20470 | Slave10 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20471 | Slave10 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20472 | Slave11 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20473 | Slave11 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20474 | Slave11 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20475 | Slave11 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20476 | Slave11 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20477 | Slave11 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20478 | Slave11 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20479 | Slave11 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20480 | Slave12 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20481 | Slave12 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20482 | Slave12 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20483 | Slave12 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20484 | Slave12 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20485 | Slave12 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20486 | Slave12 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20487 | Slave12 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20488 | Slave13 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20489 | Slave13 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20490 | Slave13 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20491 | Slave13 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20492 | Slave13 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20493 | Slave13 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20494 | Slave13 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20495 | Slave13 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20496 | Slave14 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20497 | Slave14 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20498 | Slave14 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20499 | Slave14 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20500 | Slave14 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20501 | Slave14 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20502 | Slave14 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20503 | Slave14 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20504 | Slave15 EMD-1 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20505 | Slave15 EMD-2 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20506 | Slave15 EMD-3 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20507 | Slave15 EMD-4 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20508 | Slave15 EMD-5 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20509 | Slave15 EMD-6 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20510 | Slave15 EMD-7 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20511 | Slave15 EMD-8 Temperature Calibration | RW | 2 bytes | 0:5.4; 1:+4.5C; 2:+3.2C; 3:+2.7C; 4:+1.8C; 5:+0.9C; 6:+0.0C; 7:-0.9C; 8:-1.8C; 9:-2.7C; 10:-3.2C; 11:-4.5C; 12:-5.4C
20512 | Master EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20513 | Master EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20514 | Master EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20515 | Master EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20516 | Master EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20517 | Master EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20518 | Master EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20519 | Master EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20520 | Slave01 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20521 | Slave01 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20522 | Slave01 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20523 | Slave01 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20524 | Slave01 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20525 | Slave01 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20526 | Slave01 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20527 | Slave01 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20528 | Slave02 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20529 | Slave02 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20530 | Slave02 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20531 | Slave02 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20532 | Slave02 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20533 | Slave02 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20534 | Slave02 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20535 | Slave02 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20536 | Slave03 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20537 | Slave03 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20538 | Slave03 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20539 | Slave03 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20540 | Slave03 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20541 | Slave03 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20542 | Slave03 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20543 | Slave03 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20544 | Slave04 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20545 | Slave04 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20546 | Slave04 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20547 | Slave04 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20548 | Slave04 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20549 | Slave04 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20550 | Slave04 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20551 | Slave04 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20552 | Slave05 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20553 | Slave05 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20554 | Slave05 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20555 | Slave05 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20556 | Slave05 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20557 | Slave05 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20558 | Slave05 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20559 | Slave05 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20560 | Slave06 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20561 | Slave06 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20562 | Slave06 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20563 | Slave06 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20564 | Slave06 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20565 | Slave06 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20566 | Slave06 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20567 | Slave06 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20568 | Slave07 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20569 | Slave07 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20570 | Slave07 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20571 | Slave07 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20572 | Slave07 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20573 | Slave07 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20574 | Slave07 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20575 | Slave07 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20576 | Slave08 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20577 | Slave08 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20578 | Slave08 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20579 | Slave08 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20580 | Slave08 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20581 | Slave08 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20582 | Slave08 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20583 | Slave08 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20584 | Slave09 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20585 | Slave09 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20586 | Slave09 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20587 | Slave09 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20588 | Slave09 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20589 | Slave09 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20590 | Slave09 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20591 | Slave09 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20592 | Slave10 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20593 | Slave10 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20594 | Slave10 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20595 | Slave10 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20596 | Slave10 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20597 | Slave10 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20598 | Slave10 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20599 | Slave10 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20600 | Slave11 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20601 | Slave11 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20602 | Slave11 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20603 | Slave11 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20604 | Slave11 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20605 | Slave11 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20606 | Slave11 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20607 | Slave11 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20608 | Slave12 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20609 | Slave12 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20610 | Slave12 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20611 | Slave12 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20612 | Slave12 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20613 | Slave12 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20614 | Slave12 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20615 | Slave12 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20616 | Slave13 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20617 | Slave13 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20618 | Slave13 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20619 | Slave13 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20620 | Slave13 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20621 | Slave13 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20622 | Slave13 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20623 | Slave13 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20624 | Slave14 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20625 | Slave14 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20626 | Slave14 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20627 | Slave14 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20628 | Slave14 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20629 | Slave14 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20630 | Slave14 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20631 | Slave14 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20632 | Slave15 EMD-1 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20633 | Slave15 EMD-2 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20634 | Slave15 EMD-3 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20635 | Slave15 EMD-4 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20636 | Slave15 EMD-5 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20637 | Slave15 EMD-6 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20638 | Slave15 EMD-7 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20639 | Slave15 EMD-8 Enable Humidity High Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20640 | Master EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20641 | Master EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20642 | Master EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20643 | Master EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20644 | Master EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20645 | Master EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20646 | Master EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20647 | Master EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20648 | Slave01 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20649 | Slave01 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20650 | Slave01 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20651 | Slave01 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20652 | Slave01 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20653 | Slave01 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20654 | Slave01 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20655 | Slave01 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20656 | Slave02 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20657 | Slave02 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20658 | Slave02 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20659 | Slave02 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20660 | Slave02 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20661 | Slave02 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20662 | Slave02 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20663 | Slave02 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20664 | Slave03 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20665 | Slave03 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20666 | Slave03 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20667 | Slave03 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20668 | Slave03 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20669 | Slave03 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20670 | Slave03 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20671 | Slave03 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20672 | Slave04 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20673 | Slave04 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20674 | Slave04 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20675 | Slave04 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20676 | Slave04 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20677 | Slave04 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20678 | Slave04 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20679 | Slave04 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20680 | Slave05 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20681 | Slave05 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20682 | Slave05 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20683 | Slave05 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20684 | Slave05 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20685 | Slave05 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20686 | Slave05 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20687 | Slave05 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20688 | Slave06 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20689 | Slave06 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20690 | Slave06 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20691 | Slave06 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20692 | Slave06 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20693 | Slave06 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20694 | Slave06 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20695 | Slave06 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20696 | Slave07 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20697 | Slave07 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20698 | Slave07 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20699 | Slave07 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20700 | Slave07 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20701 | Slave07 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20702 | Slave07 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20703 | Slave07 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20704 | Slave08 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20705 | Slave08 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20706 | Slave08 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20707 | Slave08 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20708 | Slave08 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20709 | Slave08 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20710 | Slave08 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20711 | Slave08 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20712 | Slave09 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20713 | Slave09 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20714 | Slave09 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20715 | Slave09 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20716 | Slave09 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20717 | Slave09 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20718 | Slave09 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20719 | Slave09 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20720 | Slave10 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20721 | Slave10 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20722 | Slave10 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20723 | Slave10 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20724 | Slave10 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20725 | Slave10 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20726 | Slave10 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20727 | Slave10 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20728 | Slave11 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20729 | Slave11 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20730 | Slave11 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20731 | Slave11 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20732 | Slave11 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20733 | Slave11 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20734 | Slave11 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20735 | Slave11 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20736 | Slave12 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20737 | Slave12 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20738 | Slave12 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20739 | Slave12 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20740 | Slave12 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20741 | Slave12 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20742 | Slave12 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20743 | Slave12 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20744 | Slave13 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20745 | Slave13 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20746 | Slave13 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20747 | Slave13 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20748 | Slave13 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20749 | Slave13 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20750 | Slave13 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20751 | Slave13 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20752 | Slave14 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20753 | Slave14 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20754 | Slave14 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20755 | Slave14 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20756 | Slave14 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20757 | Slave14 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20758 | Slave14 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20759 | Slave14 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20760 | Slave15 EMD-1 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20761 | Slave15 EMD-2 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20762 | Slave15 EMD-3 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20763 | Slave15 EMD-4 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20764 | Slave15 EMD-5 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20765 | Slave15 EMD-6 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20766 | Slave15 EMD-7 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20767 | Slave15 EMD-8 Enable Humidity Low Warining Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20768 | Master EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20769 | Master EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20770 | Master EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20771 | Master EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20772 | Master EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20773 | Master EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20774 | Master EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20775 | Master EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20776 | Slave01 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20777 | Slave01 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20778 | Slave01 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20779 | Slave01 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20780 | Slave01 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20781 | Slave01 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20782 | Slave01 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20783 | Slave01 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20784 | Slave02 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20785 | Slave02 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20786 | Slave02 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20787 | Slave02 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20788 | Slave02 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20789 | Slave02 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20790 | Slave02 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20791 | Slave02 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20792 | Slave03 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20793 | Slave03 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20794 | Slave03 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20795 | Slave03 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20796 | Slave03 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20797 | Slave03 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20798 | Slave03 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20799 | Slave03 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20800 | Slave04 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20801 | Slave04 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20802 | Slave04 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20803 | Slave04 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20804 | Slave04 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20805 | Slave04 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20806 | Slave04 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20807 | Slave04 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20808 | Slave05 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20809 | Slave05 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20810 | Slave05 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20811 | Slave05 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20812 | Slave05 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20813 | Slave05 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20814 | Slave05 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20815 | Slave05 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20816 | Slave06 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20817 | Slave06 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20818 | Slave06 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20819 | Slave06 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20820 | Slave06 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20821 | Slave06 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20822 | Slave06 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20823 | Slave06 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20824 | Slave07 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20825 | Slave07 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20826 | Slave07 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20827 | Slave07 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20828 | Slave07 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20829 | Slave07 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20830 | Slave07 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20831 | Slave07 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20832 | Slave08 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20833 | Slave08 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20834 | Slave08 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20835 | Slave08 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20836 | Slave08 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20837 | Slave08 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20838 | Slave08 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20839 | Slave08 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20840 | Slave09 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20841 | Slave09 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20842 | Slave09 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20843 | Slave09 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20844 | Slave09 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20845 | Slave09 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20846 | Slave09 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20847 | Slave09 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20848 | Slave10 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20849 | Slave10 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20850 | Slave10 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20851 | Slave10 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20852 | Slave10 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20853 | Slave10 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20854 | Slave10 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20855 | Slave10 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20856 | Slave11 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20857 | Slave11 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20858 | Slave11 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20859 | Slave11 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20860 | Slave11 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20861 | Slave11 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20862 | Slave11 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20863 | Slave11 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20864 | Slave12 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20865 | Slave12 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20866 | Slave12 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20867 | Slave12 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20868 | Slave12 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20869 | Slave12 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20870 | Slave12 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20871 | Slave12 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20872 | Slave13 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20873 | Slave13 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20874 | Slave13 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20875 | Slave13 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20876 | Slave13 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20877 | Slave13 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20878 | Slave13 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20879 | Slave13 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20880 | Slave14 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20881 | Slave14 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20882 | Slave14 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20883 | Slave14 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20884 | Slave14 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20885 | Slave14 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20886 | Slave14 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20887 | Slave14 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20888 | Slave15 EMD-1 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20889 | Slave15 EMD-2 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20890 | Slave15 EMD-3 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20891 | Slave15 EMD-4 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20892 | Slave15 EMD-5 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20893 | Slave15 EMD-6 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20894 | Slave15 EMD-7 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20895 | Slave15 EMD-8 Enable Humidity High Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20896 | Master EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20897 | Master EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20898 | Master EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20899 | Master EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20900 | Master EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20901 | Master EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20902 | Master EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20903 | Master EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20904 | Slave01 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20905 | Slave01 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20906 | Slave01 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20907 | Slave01 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20908 | Slave01 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20909 | Slave01 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20910 | Slave01 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20911 | Slave01 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20912 | Slave02 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20913 | Slave02 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20914 | Slave02 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20915 | Slave02 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20916 | Slave02 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20917 | Slave02 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20918 | Slave02 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20919 | Slave02 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20920 | Slave03 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20921 | Slave03 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20922 | Slave03 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20923 | Slave03 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20924 | Slave03 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20925 | Slave03 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20926 | Slave03 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20927 | Slave03 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20928 | Slave04 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20929 | Slave04 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20930 | Slave04 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20931 | Slave04 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20932 | Slave04 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20933 | Slave04 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20934 | Slave04 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20935 | Slave04 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20936 | Slave05 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20937 | Slave05 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20938 | Slave05 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20939 | Slave05 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20940 | Slave05 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20941 | Slave05 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20942 | Slave05 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20943 | Slave05 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20944 | Slave06 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20945 | Slave06 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20946 | Slave06 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20947 | Slave06 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20948 | Slave06 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20949 | Slave06 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20950 | Slave06 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20951 | Slave06 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20952 | Slave07 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20953 | Slave07 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20954 | Slave07 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20955 | Slave07 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20956 | Slave07 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20957 | Slave07 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20958 | Slave07 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20959 | Slave07 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20960 | Slave08 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20961 | Slave08 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20962 | Slave08 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20963 | Slave08 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20964 | Slave08 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20965 | Slave08 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20966 | Slave08 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20967 | Slave08 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20968 | Slave09 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20969 | Slave09 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20970 | Slave09 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20971 | Slave09 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20972 | Slave09 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20973 | Slave09 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20974 | Slave09 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20975 | Slave09 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20976 | Slave10 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20977 | Slave10 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20978 | Slave10 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20979 | Slave10 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20980 | Slave10 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20981 | Slave10 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20982 | Slave10 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20983 | Slave10 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20984 | Slave11 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20985 | Slave11 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20986 | Slave11 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20987 | Slave11 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20988 | Slave11 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20989 | Slave11 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20990 | Slave11 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20991 | Slave11 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20992 | Slave12 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20993 | Slave12 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20994 | Slave12 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20995 | Slave12 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20996 | Slave12 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20997 | Slave12 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20998 | Slave12 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
20999 | Slave12 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21000 | Slave13 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21001 | Slave13 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21002 | Slave13 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21003 | Slave13 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21004 | Slave13 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21005 | Slave13 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21006 | Slave13 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21007 | Slave13 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21008 | Slave14 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21009 | Slave14 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21010 | Slave14 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21011 | Slave14 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21012 | Slave14 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21013 | Slave14 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21014 | Slave14 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21015 | Slave14 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21016 | Slave15 EMD-1 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21017 | Slave15 EMD-2 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21018 | Slave15 EMD-3 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21019 | Slave15 EMD-4 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21020 | Slave15 EMD-5 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21021 | Slave15 EMD-6 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21022 | Slave15 EMD-7 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21023 | Slave15 EMD-8 Enable Humidity Low Critical Threshold | RW | 2 bytes | 1:Enable; 0:Disable
21024 | Master EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21025 | Master EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21026 | Master EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21027 | Master EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21028 | Master EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21029 | Master EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21030 | Master EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21031 | Master EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21032 | Slave01 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21033 | Slave01 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21034 | Slave01 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21035 | Slave01 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21036 | Slave01 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21037 | Slave01 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21038 | Slave01 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21039 | Slave01 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21040 | Slave02 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21041 | Slave02 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21042 | Slave02 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21043 | Slave02 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21044 | Slave02 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21045 | Slave02 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21046 | Slave02 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21047 | Slave02 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21048 | Slave03 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21049 | Slave03 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21050 | Slave03 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21051 | Slave03 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21052 | Slave03 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21053 | Slave03 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21054 | Slave03 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21055 | Slave03 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21056 | Slave04 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21057 | Slave04 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21058 | Slave04 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21059 | Slave04 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21060 | Slave04 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21061 | Slave04 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21062 | Slave04 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21063 | Slave04 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21064 | Slave05 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21065 | Slave05 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21066 | Slave05 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21067 | Slave05 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21068 | Slave05 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21069 | Slave05 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21070 | Slave05 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21071 | Slave05 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21072 | Slave06 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21073 | Slave06 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21074 | Slave06 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21075 | Slave06 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21076 | Slave06 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21077 | Slave06 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21078 | Slave06 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21079 | Slave06 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21080 | Slave07 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21081 | Slave07 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21082 | Slave07 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21083 | Slave07 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21084 | Slave07 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21085 | Slave07 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21086 | Slave07 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21087 | Slave07 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21088 | Slave08 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21089 | Slave08 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21090 | Slave08 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21091 | Slave08 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21092 | Slave08 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21093 | Slave08 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21094 | Slave08 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21095 | Slave08 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21096 | Slave09 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21097 | Slave09 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21098 | Slave09 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21099 | Slave09 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21100 | Slave09 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21101 | Slave09 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21102 | Slave09 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21103 | Slave09 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21104 | Slave10 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21105 | Slave10 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21106 | Slave10 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21107 | Slave10 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21108 | Slave10 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21109 | Slave10 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21110 | Slave10 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21111 | Slave10 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21112 | Slave11 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21113 | Slave11 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21114 | Slave11 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21115 | Slave11 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21116 | Slave11 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21117 | Slave11 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21118 | Slave11 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21119 | Slave11 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21120 | Slave12 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21121 | Slave12 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21122 | Slave12 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21123 | Slave12 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21124 | Slave12 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21125 | Slave12 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21126 | Slave12 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21127 | Slave12 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21128 | Slave13 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21129 | Slave13 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21130 | Slave13 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21131 | Slave13 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21132 | Slave13 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21133 | Slave13 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21134 | Slave13 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21135 | Slave13 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21136 | Slave14 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21137 | Slave14 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21138 | Slave14 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21139 | Slave14 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21140 | Slave14 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21141 | Slave14 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21142 | Slave14 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21143 | Slave14 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21144 | Slave15 EMD-1 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21145 | Slave15 EMD-2 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21146 | Slave15 EMD-3 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21147 | Slave15 EMD-4 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21148 | Slave15 EMD-5 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21149 | Slave15 EMD-6 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21150 | Slave15 EMD-7 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21151 | Slave15 EMD-8 Humidity High Warining Threshold | RW | 2 bytes | Unit:0.1%
21152 | Master EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21153 | Master EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21154 | Master EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21155 | Master EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21156 | Master EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21157 | Master EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21158 | Master EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21159 | Master EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21160 | Slave01 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21161 | Slave01 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21162 | Slave01 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21163 | Slave01 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21164 | Slave01 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21165 | Slave01 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21166 | Slave01 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21167 | Slave01 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21168 | Slave02 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21169 | Slave02 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21170 | Slave02 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21171 | Slave02 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21172 | Slave02 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21173 | Slave02 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21174 | Slave02 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21175 | Slave02 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21176 | Slave03 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21177 | Slave03 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21178 | Slave03 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21179 | Slave03 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21180 | Slave03 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21181 | Slave03 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21182 | Slave03 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21183 | Slave03 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21184 | Slave04 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21185 | Slave04 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21186 | Slave04 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21187 | Slave04 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21188 | Slave04 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21189 | Slave04 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21190 | Slave04 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21191 | Slave04 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21192 | Slave05 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21193 | Slave05 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21194 | Slave05 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21195 | Slave05 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21196 | Slave05 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21197 | Slave05 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21198 | Slave05 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21199 | Slave05 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21200 | Slave06 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21201 | Slave06 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21202 | Slave06 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21203 | Slave06 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21204 | Slave06 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21205 | Slave06 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21206 | Slave06 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21207 | Slave06 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21208 | Slave07 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21209 | Slave07 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21210 | Slave07 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21211 | Slave07 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21212 | Slave07 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21213 | Slave07 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21214 | Slave07 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21215 | Slave07 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21216 | Slave08 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21217 | Slave08 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21218 | Slave08 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21219 | Slave08 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21220 | Slave08 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21221 | Slave08 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21222 | Slave08 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21223 | Slave08 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21224 | Slave09 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21225 | Slave09 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21226 | Slave09 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21227 | Slave09 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21228 | Slave09 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21229 | Slave09 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21230 | Slave09 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21231 | Slave09 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21232 | Slave10 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21233 | Slave10 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21234 | Slave10 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21235 | Slave10 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21236 | Slave10 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21237 | Slave10 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21238 | Slave10 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21239 | Slave10 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21240 | Slave11 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21241 | Slave11 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21242 | Slave11 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21243 | Slave11 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21244 | Slave11 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21245 | Slave11 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21246 | Slave11 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21247 | Slave11 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21248 | Slave12 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21249 | Slave12 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21250 | Slave12 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21251 | Slave12 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21252 | Slave12 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21253 | Slave12 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21254 | Slave12 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21255 | Slave12 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21256 | Slave13 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21257 | Slave13 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21258 | Slave13 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21259 | Slave13 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21260 | Slave13 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21261 | Slave13 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21262 | Slave13 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21263 | Slave13 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21264 | Slave14 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21265 | Slave14 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21266 | Slave14 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21267 | Slave14 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21268 | Slave14 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21269 | Slave14 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21270 | Slave14 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21271 | Slave14 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21272 | Slave15 EMD-1 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21273 | Slave15 EMD-2 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21274 | Slave15 EMD-3 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21275 | Slave15 EMD-4 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21276 | Slave15 EMD-5 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21277 | Slave15 EMD-6 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21278 | Slave15 EMD-7 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21279 | Slave15 EMD-8 Humidity Low Warining Threshold | RW | 2 bytes | Unit:0.1%
21280 | Master EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21281 | Master EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21282 | Master EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21283 | Master EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21284 | Master EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21285 | Master EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21286 | Master EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21287 | Master EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21288 | Slave01 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21289 | Slave01 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21290 | Slave01 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21291 | Slave01 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21292 | Slave01 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21293 | Slave01 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21294 | Slave01 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21295 | Slave01 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21296 | Slave02 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21297 | Slave02 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21298 | Slave02 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21299 | Slave02 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21300 | Slave02 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21301 | Slave02 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21302 | Slave02 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21303 | Slave02 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21304 | Slave03 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21305 | Slave03 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21306 | Slave03 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21307 | Slave03 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21308 | Slave03 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21309 | Slave03 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21310 | Slave03 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21311 | Slave03 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21312 | Slave04 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21313 | Slave04 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21314 | Slave04 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21315 | Slave04 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21316 | Slave04 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21317 | Slave04 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21318 | Slave04 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21319 | Slave04 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21320 | Slave05 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21321 | Slave05 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21322 | Slave05 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21323 | Slave05 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21324 | Slave05 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21325 | Slave05 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21326 | Slave05 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21327 | Slave05 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21328 | Slave06 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21329 | Slave06 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21330 | Slave06 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21331 | Slave06 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21332 | Slave06 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21333 | Slave06 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21334 | Slave06 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21335 | Slave06 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21336 | Slave07 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21337 | Slave07 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21338 | Slave07 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21339 | Slave07 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21340 | Slave07 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21341 | Slave07 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21342 | Slave07 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21343 | Slave07 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21344 | Slave08 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21345 | Slave08 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21346 | Slave08 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21347 | Slave08 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21348 | Slave08 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21349 | Slave08 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21350 | Slave08 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21351 | Slave08 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21352 | Slave09 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21353 | Slave09 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21354 | Slave09 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21355 | Slave09 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21356 | Slave09 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21357 | Slave09 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21358 | Slave09 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21359 | Slave09 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21360 | Slave10 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21361 | Slave10 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21362 | Slave10 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21363 | Slave10 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21364 | Slave10 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21365 | Slave10 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21366 | Slave10 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21367 | Slave10 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21368 | Slave11 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21369 | Slave11 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21370 | Slave11 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21371 | Slave11 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21372 | Slave11 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21373 | Slave11 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21374 | Slave11 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21375 | Slave11 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21376 | Slave12 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21377 | Slave12 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21378 | Slave12 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21379 | Slave12 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21380 | Slave12 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21381 | Slave12 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21382 | Slave12 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21383 | Slave12 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21384 | Slave13 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21385 | Slave13 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21386 | Slave13 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21387 | Slave13 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21388 | Slave13 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21389 | Slave13 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21390 | Slave13 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21391 | Slave13 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21392 | Slave14 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21393 | Slave14 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21394 | Slave14 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21395 | Slave14 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21396 | Slave14 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21397 | Slave14 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21398 | Slave14 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21399 | Slave14 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21400 | Slave15 EMD-1 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21401 | Slave15 EMD-2 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21402 | Slave15 EMD-3 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21403 | Slave15 EMD-4 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21404 | Slave15 EMD-5 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21405 | Slave15 EMD-6 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21406 | Slave15 EMD-7 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21407 | Slave15 EMD-8 Humidity High Critical Threshold | RW | 2 bytes | Unit:0.1%
21408 | Master EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21409 | Master EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21410 | Master EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21411 | Master EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21412 | Master EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21413 | Master EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21414 | Master EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21415 | Master EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21416 | Slave01 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21417 | Slave01 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21418 | Slave01 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21419 | Slave01 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21420 | Slave01 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21421 | Slave01 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21422 | Slave01 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21423 | Slave01 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21424 | Slave02 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21425 | Slave02 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21426 | Slave02 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21427 | Slave02 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21428 | Slave02 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21429 | Slave02 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21430 | Slave02 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21431 | Slave02 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21432 | Slave03 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21433 | Slave03 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21434 | Slave03 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21435 | Slave03 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21436 | Slave03 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21437 | Slave03 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21438 | Slave03 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21439 | Slave03 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21440 | Slave04 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21441 | Slave04 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21442 | Slave04 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21443 | Slave04 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21444 | Slave04 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21445 | Slave04 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21446 | Slave04 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21447 | Slave04 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21448 | Slave05 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21449 | Slave05 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21450 | Slave05 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21451 | Slave05 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21452 | Slave05 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21453 | Slave05 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21454 | Slave05 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21455 | Slave05 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21456 | Slave06 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21457 | Slave06 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21458 | Slave06 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21459 | Slave06 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21460 | Slave06 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21461 | Slave06 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21462 | Slave06 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21463 | Slave06 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21464 | Slave07 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21465 | Slave07 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21466 | Slave07 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21467 | Slave07 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21468 | Slave07 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21469 | Slave07 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21470 | Slave07 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21471 | Slave07 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21472 | Slave08 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21473 | Slave08 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21474 | Slave08 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21475 | Slave08 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21476 | Slave08 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21477 | Slave08 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21478 | Slave08 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21479 | Slave08 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21480 | Slave09 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21481 | Slave09 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21482 | Slave09 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21483 | Slave09 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21484 | Slave09 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21485 | Slave09 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21486 | Slave09 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21487 | Slave09 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21488 | Slave10 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21489 | Slave10 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21490 | Slave10 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21491 | Slave10 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21492 | Slave10 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21493 | Slave10 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21494 | Slave10 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21495 | Slave10 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21496 | Slave11 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21497 | Slave11 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21498 | Slave11 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21499 | Slave11 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21500 | Slave11 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21501 | Slave11 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21502 | Slave11 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21503 | Slave11 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21504 | Slave12 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21505 | Slave12 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21506 | Slave12 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21507 | Slave12 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21508 | Slave12 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21509 | Slave12 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21510 | Slave12 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21511 | Slave12 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21512 | Slave13 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21513 | Slave13 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21514 | Slave13 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21515 | Slave13 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21516 | Slave13 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21517 | Slave13 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21518 | Slave13 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21519 | Slave13 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21520 | Slave14 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21521 | Slave14 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21522 | Slave14 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21523 | Slave14 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21524 | Slave14 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21525 | Slave14 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21526 | Slave14 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21527 | Slave14 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21528 | Slave15 EMD-1 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21529 | Slave15 EMD-2 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21530 | Slave15 EMD-3 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21531 | Slave15 EMD-4 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21532 | Slave15 EMD-5 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21533 | Slave15 EMD-6 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21534 | Slave15 EMD-7 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21535 | Slave15 EMD-8 Humidity Low Critical Threshold | RW | 2 bytes | Unit:0.1%
21536 | Master EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21537 | Master EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21538 | Master EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21539 | Master EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21540 | Master EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21541 | Master EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21542 | Master EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21543 | Master EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21544 | Slave01 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21545 | Slave01 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21546 | Slave01 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21547 | Slave01 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21548 | Slave01 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21549 | Slave01 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21550 | Slave01 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21551 | Slave01 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21552 | Slave02 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21553 | Slave02 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21554 | Slave02 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21555 | Slave02 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21556 | Slave02 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21557 | Slave02 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21558 | Slave02 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21559 | Slave02 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21560 | Slave03 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21561 | Slave03 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21562 | Slave03 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21563 | Slave03 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21564 | Slave03 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21565 | Slave03 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21566 | Slave03 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21567 | Slave03 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21568 | Slave04 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21569 | Slave04 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21570 | Slave04 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21571 | Slave04 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21572 | Slave04 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21573 | Slave04 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21574 | Slave04 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21575 | Slave04 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21576 | Slave05 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21577 | Slave05 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21578 | Slave05 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21579 | Slave05 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21580 | Slave05 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21581 | Slave05 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21582 | Slave05 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21583 | Slave05 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21584 | Slave06 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21585 | Slave06 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21586 | Slave06 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21587 | Slave06 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21588 | Slave06 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21589 | Slave06 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21590 | Slave06 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21591 | Slave06 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21592 | Slave07 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21593 | Slave07 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21594 | Slave07 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21595 | Slave07 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21596 | Slave07 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21597 | Slave07 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21598 | Slave07 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21599 | Slave07 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21600 | Slave08 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21601 | Slave08 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21602 | Slave08 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21603 | Slave08 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21604 | Slave08 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21605 | Slave08 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21606 | Slave08 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21607 | Slave08 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21608 | Slave09 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21609 | Slave09 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21610 | Slave09 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21611 | Slave09 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21612 | Slave09 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21613 | Slave09 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21614 | Slave09 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21615 | Slave09 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21616 | Slave10 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21617 | Slave10 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21618 | Slave10 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21619 | Slave10 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21620 | Slave10 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21621 | Slave10 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21622 | Slave10 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21623 | Slave10 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21624 | Slave11 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21625 | Slave11 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21626 | Slave11 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21627 | Slave11 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21628 | Slave11 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21629 | Slave11 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21630 | Slave11 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21631 | Slave11 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21632 | Slave12 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21633 | Slave12 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21634 | Slave12 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21635 | Slave12 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21636 | Slave12 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21637 | Slave12 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21638 | Slave12 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21639 | Slave12 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21640 | Slave13 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21641 | Slave13 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21642 | Slave13 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21643 | Slave13 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21644 | Slave13 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21645 | Slave13 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21646 | Slave13 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21647 | Slave13 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21648 | Slave14 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21649 | Slave14 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21650 | Slave14 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21651 | Slave14 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21652 | Slave14 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21653 | Slave14 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21654 | Slave14 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21655 | Slave14 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21656 | Slave15 EMD-1 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21657 | Slave15 EMD-2 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21658 | Slave15 EMD-3 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21659 | Slave15 EMD-4 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21660 | Slave15 EMD-5 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21661 | Slave15 EMD-6 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21662 | Slave15 EMD-7 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21663 | Slave15 EMD-8 Humidity Calibration | RW | 2 bytes | 0:+6%; 1:+5%; 2:+4%; 3:+3%; 4:+2%; 5:+1%; 6:+0%; 7:-1%; 8:-2%; 9:-3%; 10:-4%; 11:-5%; 12:-6%;
21664 | Master EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21665 | Master EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21666 | Master EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21667 | Master EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21668 | Master EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21669 | Master EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21670 | Master EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21671 | Master EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21672 | Slave01 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21673 | Slave01 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21674 | Slave01 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21675 | Slave01 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21676 | Slave01 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21677 | Slave01 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21678 | Slave01 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21679 | Slave01 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21680 | Slave02 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21681 | Slave02 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21682 | Slave02 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21683 | Slave02 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21684 | Slave02 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21685 | Slave02 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21686 | Slave02 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21687 | Slave02 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21688 | Slave03 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21689 | Slave03 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21690 | Slave03 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21691 | Slave03 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21692 | Slave03 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21693 | Slave03 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21694 | Slave03 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21695 | Slave03 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21696 | Slave04 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21697 | Slave04 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21698 | Slave04 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21699 | Slave04 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21700 | Slave04 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21701 | Slave04 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21702 | Slave04 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21703 | Slave04 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21704 | Slave05 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21705 | Slave05 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21706 | Slave05 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21707 | Slave05 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21708 | Slave05 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21709 | Slave05 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21710 | Slave05 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21711 | Slave05 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21712 | Slave06 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21713 | Slave06 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21714 | Slave06 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21715 | Slave06 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21716 | Slave06 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21717 | Slave06 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21718 | Slave06 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21719 | Slave06 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21720 | Slave07 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21721 | Slave07 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21722 | Slave07 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21723 | Slave07 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21724 | Slave07 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21725 | Slave07 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21726 | Slave07 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21727 | Slave07 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21728 | Slave08 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21729 | Slave08 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21730 | Slave08 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21731 | Slave08 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21732 | Slave08 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21733 | Slave08 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21734 | Slave08 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21735 | Slave08 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21736 | Slave09 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21737 | Slave09 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21738 | Slave09 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21739 | Slave09 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21740 | Slave09 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21741 | Slave09 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21742 | Slave09 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21743 | Slave09 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21744 | Slave10 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21745 | Slave10 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21746 | Slave10 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21747 | Slave10 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21748 | Slave10 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21749 | Slave10 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21750 | Slave10 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21751 | Slave10 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21752 | Slave11 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21753 | Slave11 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21754 | Slave11 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21755 | Slave11 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21756 | Slave11 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21757 | Slave11 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21758 | Slave11 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21759 | Slave11 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21760 | Slave12 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21761 | Slave12 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21762 | Slave12 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21763 | Slave12 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21764 | Slave12 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21765 | Slave12 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21766 | Slave12 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21767 | Slave12 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21768 | Slave13 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21769 | Slave13 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21770 | Slave13 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21771 | Slave13 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21772 | Slave13 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21773 | Slave13 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21774 | Slave13 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21775 | Slave13 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21776 | Slave14 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21777 | Slave14 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21778 | Slave14 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21779 | Slave14 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21780 | Slave14 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21781 | Slave14 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21782 | Slave14 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21783 | Slave14 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21784 | Slave15 EMD-1 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21785 | Slave15 EMD-2 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21786 | Slave15 EMD-3 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21787 | Slave15 EMD-4 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21788 | Slave15 EMD-5 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21789 | Slave15 EMD-6 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21790 | Slave15 EMD-7 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21791 | Slave15 EMD-8 Alarm1 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21792 | Master EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21793 | Master EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21794 | Master EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21795 | Master EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21796 | Master EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21797 | Master EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21798 | Master EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21799 | Master EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21800 | Slave01 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21801 | Slave01 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21802 | Slave01 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21803 | Slave01 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21804 | Slave01 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21805 | Slave01 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21806 | Slave01 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21807 | Slave01 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21808 | Slave02 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21809 | Slave02 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21810 | Slave02 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21811 | Slave02 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21812 | Slave02 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21813 | Slave02 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21814 | Slave02 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21815 | Slave02 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21816 | Slave03 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21817 | Slave03 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21818 | Slave03 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21819 | Slave03 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21820 | Slave03 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21821 | Slave03 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21822 | Slave03 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21823 | Slave03 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21824 | Slave04 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21825 | Slave04 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21826 | Slave04 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21827 | Slave04 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21828 | Slave04 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21829 | Slave04 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21830 | Slave04 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21831 | Slave04 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21832 | Slave05 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21833 | Slave05 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21834 | Slave05 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21835 | Slave05 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21836 | Slave05 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21837 | Slave05 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21838 | Slave05 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21839 | Slave05 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21840 | Slave06 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21841 | Slave06 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21842 | Slave06 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21843 | Slave06 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21844 | Slave06 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21845 | Slave06 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21846 | Slave06 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21847 | Slave06 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21848 | Slave07 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21849 | Slave07 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21850 | Slave07 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21851 | Slave07 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21852 | Slave07 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21853 | Slave07 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21854 | Slave07 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21855 | Slave07 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21856 | Slave08 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21857 | Slave08 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21858 | Slave08 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21859 | Slave08 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21860 | Slave08 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21861 | Slave08 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21862 | Slave08 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21863 | Slave08 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21864 | Slave09 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21865 | Slave09 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21866 | Slave09 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21867 | Slave09 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21868 | Slave09 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21869 | Slave09 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21870 | Slave09 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21871 | Slave09 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21872 | Slave10 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21873 | Slave10 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21874 | Slave10 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21875 | Slave10 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21876 | Slave10 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21877 | Slave10 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21878 | Slave10 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21879 | Slave10 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21880 | Slave11 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21881 | Slave11 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21882 | Slave11 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21883 | Slave11 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21884 | Slave11 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21885 | Slave11 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21886 | Slave11 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21887 | Slave11 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21888 | Slave12 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21889 | Slave12 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21890 | Slave12 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21891 | Slave12 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21892 | Slave12 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21893 | Slave12 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21894 | Slave12 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21895 | Slave12 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21896 | Slave13 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21897 | Slave13 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21898 | Slave13 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21899 | Slave13 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21900 | Slave13 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21901 | Slave13 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21902 | Slave13 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21903 | Slave13 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21904 | Slave14 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21905 | Slave14 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21906 | Slave14 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21907 | Slave14 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21908 | Slave14 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21909 | Slave14 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21910 | Slave14 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21911 | Slave14 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21912 | Slave15 EMD-1 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21913 | Slave15 EMD-2 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21914 | Slave15 EMD-3 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21915 | Slave15 EMD-4 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21916 | Slave15 EMD-5 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21917 | Slave15 EMD-6 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21918 | Slave15 EMD-7 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21919 | Slave15 EMD-8 Alarm2 Setup | RW | 2 bytes | 0:disabled; 1:normal open; 2:normal close
21920 | Master Inlet Over Load Warning | RW | 4 bytes | Unit:1
21922 | Slave01 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21924 | Slave02 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21926 | Slave03 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21928 | Slave04 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21930 | Slave05 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21932 | Slave06 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21934 | Slave07 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21936 | Slave08 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21938 | Slave09 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21940 | Slave10 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21942 | Slave11 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21944 | Slave12 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21946 | Slave13 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21948 | Slave14 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21950 | Slave15 Inlet Over Load Warning | RW | 4 bytes | Unit:1
21952 | Master Inlet Over Load Critical | RW | 4 bytes | Unit:1
21954 | Slave01 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21956 | Slave02 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21958 | Slave03 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21960 | Slave04 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21962 | Slave05 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21964 | Slave06 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21966 | Slave07 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21968 | Slave08 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21970 | Slave09 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21972 | Slave10 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21974 | Slave11 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21976 | Slave12 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21978 | Slave13 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21980 | Slave14 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21982 | Slave15 Inlet Over Load Critical | RW | 4 bytes | Unit:1
21984 | Master Inlet Name | RW | 32 bytes
22000 | Slave01 Inlet Name | RW | 32 bytes
22016 | Slave02 Inlet Name | RW | 32 bytes
22032 | Slave03 Inlet Name | RW | 32 bytes
22048 | Slave04 Inlet Name | RW | 32 bytes
22064 | Slave05 Inlet Name | RW | 32 bytes
22080 | Slave06 Inlet Name | RW | 32 bytes
22096 | Slave07 Inlet Name | RW | 32 bytes
22112 | Slave08 Inlet Name | RW | 32 bytes
22128 | Slave09 Inlet Name | RW | 32 bytes
22144 | Slave10 Inlet Name | RW | 32 bytes
22160 | Slave11 Inlet Name | RW | 32 bytes
22176 | Slave12 Inlet Name | RW | 32 bytes
22192 | Slave13 Inlet Name | RW | 32 bytes
22208 | Slave14 Inlet Name | RW | 32 bytes
22224 | Slave15 Inlet Name | RW | 32 bytes
22240 | Master Outlet Port01 Name | RW | 32 bytes
22256 | Master Outlet Port02 Name | RW | 32 bytes
22272 | Master Outlet Port03 Name | RW | 32 bytes
22288 | Master Outlet Port04 Name | RW | 32 bytes
22304 | Master Outlet Port05 Name | RW | 32 bytes
22320 | Master Outlet Port06 Name | RW | 32 bytes
22336 | Master Outlet Port07 Name | RW | 32 bytes
22352 | Master Outlet Port08 Name | RW | 32 bytes
22368 | Master Outlet Port09 Name | RW | 32 bytes
22384 | Master Outlet Port10 Name | RW | 32 bytes
22400 | Master Outlet Port11 Name | RW | 32 bytes
22416 | Master Outlet Port12 Name | RW | 32 bytes
22432 | Master Outlet Port13 Name | RW | 32 bytes
22448 | Master Outlet Port14 Name | RW | 32 bytes
22464 | Master Outlet Port15 Name | RW | 32 bytes
22480 | Master Outlet Port16 Name | RW | 32 bytes
22496 | Master Outlet Port17 Name | RW | 32 bytes
22512 | Master Outlet Port18 Name | RW | 32 bytes
22528 | Master Outlet Port19 Name | RW | 32 bytes
22544 | Master Outlet Port20 Name | RW | 32 bytes
22560 | Master Outlet Port21 Name | RW | 32 bytes
22576 | Master Outlet Port22 Name | RW | 32 bytes
22592 | Master Outlet Port23 Name | RW | 32 bytes
22608 | Master Outlet Port24 Name | RW | 32 bytes
22624 | Master Outlet Port25 Name | RW | 32 bytes
22640 | Master Outlet Port26 Name | RW | 32 bytes
22656 | Master Outlet Port27 Name | RW | 32 bytes
22672 | Master Outlet Port28 Name | RW | 32 bytes
22688 | Master Outlet Port29 Name | RW | 32 bytes
22704 | Master Outlet Port30 Name | RW | 32 bytes
22720 | Master Outlet Port31 Name | RW | 32 bytes
22736 | Master Outlet Port32 Name | RW | 32 bytes
22752 | Master Outlet Port33 Name | RW | 32 bytes
22768 | Master Outlet Port34 Name | RW | 32 bytes
22784 | Master Outlet Port35 Name | RW | 32 bytes
22800 | Master Outlet Port36 Name | RW | 32 bytes
22816 | Master Outlet Port37 Name | RW | 32 bytes
22832 | Master Outlet Port38 Name | RW | 32 bytes
22848 | Master Outlet Port39 Name | RW | 32 bytes
22864 | Master Outlet Port40 Name | RW | 32 bytes
22880 | Master Outlet Port41 Name | RW | 32 bytes
22896 | Master Outlet Port42 Name | RW | 32 bytes
22912 | Master Outlet Port43 Name | RW | 32 bytes
22928 | Master Outlet Port44 Name | RW | 32 bytes
22944 | Master Outlet Port45 Name | RW | 32 bytes
22960 | Master Outlet Port46 Name | RW | 32 bytes
22976 | Master Outlet Port47 Name | RW | 32 bytes
22992 | Master Outlet Port48 Name | RW | 32 bytes
23008 | Slave01 Outlet Port01 Name | RW | 32 bytes
23024 | Slave01 Outlet Port02 Name | RW | 32 bytes
23040 | Slave01 Outlet Port03 Name | RW | 32 bytes
23056 | Slave01 Outlet Port04 Name | RW | 32 bytes
23072 | Slave01 Outlet Port05 Name | RW | 32 bytes
23088 | Slave01 Outlet Port06 Name | RW | 32 bytes
23104 | Slave01 Outlet Port07 Name | RW | 32 bytes
23120 | Slave01 Outlet Port08 Name | RW | 32 bytes
23136 | Slave01 Outlet Port09 Name | RW | 32 bytes
23152 | Slave01 Outlet Port10 Name | RW | 32 bytes
23168 | Slave01 Outlet Port11 Name | RW | 32 bytes
23184 | Slave01 Outlet Port12 Name | RW | 32 bytes
23200 | Slave01 Outlet Port13 Name | RW | 32 bytes
23216 | Slave01 Outlet Port14 Name | RW | 32 bytes
23232 | Slave01 Outlet Port15 Name | RW | 32 bytes
23248 | Slave01 Outlet Port16 Name | RW | 32 bytes
23264 | Slave01 Outlet Port17 Name | RW | 32 bytes
23280 | Slave01 Outlet Port18 Name | RW | 32 bytes
23296 | Slave01 Outlet Port19 Name | RW | 32 bytes
23312 | Slave01 Outlet Port20 Name | RW | 32 bytes
23328 | Slave01 Outlet Port21 Name | RW | 32 bytes
23344 | Slave01 Outlet Port22 Name | RW | 32 bytes
23360 | Slave01 Outlet Port23 Name | RW | 32 bytes
23376 | Slave01 Outlet Port24 Name | RW | 32 bytes
23392 | Slave01 Outlet Port25 Name | RW | 32 bytes
23408 | Slave01 Outlet Port26 Name | RW | 32 bytes
23424 | Slave01 Outlet Port27 Name | RW | 32 bytes
23440 | Slave01 Outlet Port28 Name | RW | 32 bytes
23456 | Slave01 Outlet Port29 Name | RW | 32 bytes
23472 | Slave01 Outlet Port30 Name | RW | 32 bytes
23488 | Slave01 Outlet Port31 Name | RW | 32 bytes
23504 | Slave01 Outlet Port32 Name | RW | 32 bytes
23520 | Slave01 Outlet Port33 Name | RW | 32 bytes
23536 | Slave01 Outlet Port34 Name | RW | 32 bytes
23552 | Slave01 Outlet Port35 Name | RW | 32 bytes
23568 | Slave01 Outlet Port36 Name | RW | 32 bytes
23584 | Slave01 Outlet Port37 Name | RW | 32 bytes
23600 | Slave01 Outlet Port38 Name | RW | 32 bytes
23616 | Slave01 Outlet Port39 Name | RW | 32 bytes
23632 | Slave01 Outlet Port40 Name | RW | 32 bytes
23648 | Slave01 Outlet Port41 Name | RW | 32 bytes
23664 | Slave01 Outlet Port42 Name | RW | 32 bytes
23680 | Slave01 Outlet Port43 Name | RW | 32 bytes
23696 | Slave01 Outlet Port44 Name | RW | 32 bytes
23712 | Slave01 Outlet Port45 Name | RW | 32 bytes
23728 | Slave01 Outlet Port46 Name | RW | 32 bytes
23744 | Slave01 Outlet Port47 Name | RW | 32 bytes
23760 | Slave01 Outlet Port48 Name | RW | 32 bytes
23776 | Slave02 Outlet Port01 Name | RW | 32 bytes
23792 | Slave02 Outlet Port02 Name | RW | 32 bytes
23808 | Slave02 Outlet Port03 Name | RW | 32 bytes
23824 | Slave02 Outlet Port04 Name | RW | 32 bytes
23840 | Slave02 Outlet Port05 Name | RW | 32 bytes
23856 | Slave02 Outlet Port06 Name | RW | 32 bytes
23872 | Slave02 Outlet Port07 Name | RW | 32 bytes
23888 | Slave02 Outlet Port08 Name | RW | 32 bytes
23904 | Slave02 Outlet Port09 Name | RW | 32 bytes
23920 | Slave02 Outlet Port10 Name | RW | 32 bytes
23936 | Slave02 Outlet Port11 Name | RW | 32 bytes
23952 | Slave02 Outlet Port12 Name | RW | 32 bytes
23968 | Slave02 Outlet Port13 Name | RW | 32 bytes
23984 | Slave02 Outlet Port14 Name | RW | 32 bytes
24000 | Slave02 Outlet Port15 Name | RW | 32 bytes
24016 | Slave02 Outlet Port16 Name | RW | 32 bytes
24032 | Slave02 Outlet Port17 Name | RW | 32 bytes
24048 | Slave02 Outlet Port18 Name | RW | 32 bytes
24064 | Slave02 Outlet Port19 Name | RW | 32 bytes
24080 | Slave02 Outlet Port20 Name | RW | 32 bytes
24096 | Slave02 Outlet Port21 Name | RW | 32 bytes
24112 | Slave02 Outlet Port22 Name | RW | 32 bytes
24128 | Slave02 Outlet Port23 Name | RW | 32 bytes
24144 | Slave02 Outlet Port24 Name | RW | 32 bytes
24160 | Slave02 Outlet Port25 Name | RW | 32 bytes
24176 | Slave02 Outlet Port26 Name | RW | 32 bytes
24192 | Slave02 Outlet Port27 Name | RW | 32 bytes
24208 | Slave02 Outlet Port28 Name | RW | 32 bytes
24224 | Slave02 Outlet Port29 Name | RW | 32 bytes
24240 | Slave02 Outlet Port30 Name | RW | 32 bytes
24256 | Slave02 Outlet Port31 Name | RW | 32 bytes
24272 | Slave02 Outlet Port32 Name | RW | 32 bytes
24288 | Slave02 Outlet Port33 Name | RW | 32 bytes
24304 | Slave02 Outlet Port34 Name | RW | 32 bytes
24320 | Slave02 Outlet Port35 Name | RW | 32 bytes
24336 | Slave02 Outlet Port36 Name | RW | 32 bytes
24352 | Slave02 Outlet Port37 Name | RW | 32 bytes
24368 | Slave02 Outlet Port38 Name | RW | 32 bytes
24384 | Slave02 Outlet Port39 Name | RW | 32 bytes
24400 | Slave02 Outlet Port40 Name | RW | 32 bytes
24416 | Slave02 Outlet Port41 Name | RW | 32 bytes
24432 | Slave02 Outlet Port42 Name | RW | 32 bytes
24448 | Slave02 Outlet Port43 Name | RW | 32 bytes
24464 | Slave02 Outlet Port44 Name | RW | 32 bytes
24480 | Slave02 Outlet Port45 Name | RW | 32 bytes
24496 | Slave02 Outlet Port46 Name | RW | 32 bytes
24512 | Slave02 Outlet Port47 Name | RW | 32 bytes
24528 | Slave02 Outlet Port48 Name | RW | 32 bytes
24544 | Slave03 Outlet Port01 Name | RW | 32 bytes
24560 | Slave03 Outlet Port02 Name | RW | 32 bytes
24576 | Slave03 Outlet Port03 Name | RW | 32 bytes
24592 | Slave03 Outlet Port04 Name | RW | 32 bytes
24608 | Slave03 Outlet Port05 Name | RW | 32 bytes
24624 | Slave03 Outlet Port06 Name | RW | 32 bytes
24640 | Slave03 Outlet Port07 Name | RW | 32 bytes
24656 | Slave03 Outlet Port08 Name | RW | 32 bytes
24672 | Slave03 Outlet Port09 Name | RW | 32 bytes
24688 | Slave03 Outlet Port10 Name | RW | 32 bytes
24704 | Slave03 Outlet Port11 Name | RW | 32 bytes
24720 | Slave03 Outlet Port12 Name | RW | 32 bytes
24736 | Slave03 Outlet Port13 Name | RW | 32 bytes
24752 | Slave03 Outlet Port14 Name | RW | 32 bytes
24768 | Slave03 Outlet Port15 Name | RW | 32 bytes
24784 | Slave03 Outlet Port16 Name | RW | 32 bytes
24800 | Slave03 Outlet Port17 Name | RW | 32 bytes
24816 | Slave03 Outlet Port18 Name | RW | 32 bytes
24832 | Slave03 Outlet Port19 Name | RW | 32 bytes
24848 | Slave03 Outlet Port20 Name | RW | 32 bytes
24864 | Slave03 Outlet Port21 Name | RW | 32 bytes
24880 | Slave03 Outlet Port22 Name | RW | 32 bytes
24896 | Slave03 Outlet Port23 Name | RW | 32 bytes
24912 | Slave03 Outlet Port24 Name | RW | 32 bytes
24928 | Slave03 Outlet Port25 Name | RW | 32 bytes
24944 | Slave03 Outlet Port26 Name | RW | 32 bytes
24960 | Slave03 Outlet Port27 Name | RW | 32 bytes
24976 | Slave03 Outlet Port28 Name | RW | 32 bytes
24992 | Slave03 Outlet Port29 Name | RW | 32 bytes
25008 | Slave03 Outlet Port30 Name | RW | 32 bytes
25024 | Slave03 Outlet Port31 Name | RW | 32 bytes
25040 | Slave03 Outlet Port32 Name | RW | 32 bytes
25056 | Slave03 Outlet Port33 Name | RW | 32 bytes
25072 | Slave03 Outlet Port34 Name | RW | 32 bytes
25088 | Slave03 Outlet Port35 Name | RW | 32 bytes
25104 | Slave03 Outlet Port36 Name | RW | 32 bytes
25120 | Slave03 Outlet Port37 Name | RW | 32 bytes
25136 | Slave03 Outlet Port38 Name | RW | 32 bytes
25152 | Slave03 Outlet Port39 Name | RW | 32 bytes
25168 | Slave03 Outlet Port40 Name | RW | 32 bytes
25184 | Slave03 Outlet Port41 Name | RW | 32 bytes
25200 | Slave03 Outlet Port42 Name | RW | 32 bytes
25216 | Slave03 Outlet Port43 Name | RW | 32 bytes
25232 | Slave03 Outlet Port44 Name | RW | 32 bytes
25248 | Slave03 Outlet Port45 Name | RW | 32 bytes
25264 | Slave03 Outlet Port46 Name | RW | 32 bytes
25280 | Slave03 Outlet Port47 Name | RW | 32 bytes
25296 | Slave03 Outlet Port48 Name | RW | 32 bytes
25312 | Slave04 Outlet Port01 Name | RW | 32 bytes
25328 | Slave04 Outlet Port02 Name | RW | 32 bytes
25344 | Slave04 Outlet Port03 Name | RW | 32 bytes
25360 | Slave04 Outlet Port04 Name | RW | 32 bytes
25376 | Slave04 Outlet Port05 Name | RW | 32 bytes
25392 | Slave04 Outlet Port06 Name | RW | 32 bytes
25408 | Slave04 Outlet Port07 Name | RW | 32 bytes
25424 | Slave04 Outlet Port08 Name | RW | 32 bytes
25440 | Slave04 Outlet Port09 Name | RW | 32 bytes
25456 | Slave04 Outlet Port10 Name | RW | 32 bytes
25472 | Slave04 Outlet Port11 Name | RW | 32 bytes
25488 | Slave04 Outlet Port12 Name | RW | 32 bytes
25504 | Slave04 Outlet Port13 Name | RW | 32 bytes
25520 | Slave04 Outlet Port14 Name | RW | 32 bytes
25536 | Slave04 Outlet Port15 Name | RW | 32 bytes
25552 | Slave04 Outlet Port16 Name | RW | 32 bytes
25568 | Slave04 Outlet Port17 Name | RW | 32 bytes
25584 | Slave04 Outlet Port18 Name | RW | 32 bytes
25600 | Slave04 Outlet Port19 Name | RW | 32 bytes
25616 | Slave04 Outlet Port20 Name | RW | 32 bytes
25632 | Slave04 Outlet Port21 Name | RW | 32 bytes
25648 | Slave04 Outlet Port22 Name | RW | 32 bytes
25664 | Slave04 Outlet Port23 Name | RW | 32 bytes
25680 | Slave04 Outlet Port24 Name | RW | 32 bytes
25696 | Slave04 Outlet Port25 Name | RW | 32 bytes
25712 | Slave04 Outlet Port26 Name | RW | 32 bytes
25728 | Slave04 Outlet Port27 Name | RW | 32 bytes
25744 | Slave04 Outlet Port28 Name | RW | 32 bytes
25760 | Slave04 Outlet Port29 Name | RW | 32 bytes
25776 | Slave04 Outlet Port30 Name | RW | 32 bytes
25792 | Slave04 Outlet Port31 Name | RW | 32 bytes
25808 | Slave04 Outlet Port32 Name | RW | 32 bytes
25824 | Slave04 Outlet Port33 Name | RW | 32 bytes
25840 | Slave04 Outlet Port34 Name | RW | 32 bytes
25856 | Slave04 Outlet Port35 Name | RW | 32 bytes
25872 | Slave04 Outlet Port36 Name | RW | 32 bytes
25888 | Slave04 Outlet Port37 Name | RW | 32 bytes
25904 | Slave04 Outlet Port38 Name | RW | 32 bytes
25920 | Slave04 Outlet Port39 Name | RW | 32 bytes
25936 | Slave04 Outlet Port40 Name | RW | 32 bytes
25952 | Slave04 Outlet Port41 Name | RW | 32 bytes
25968 | Slave04 Outlet Port42 Name | RW | 32 bytes
25984 | Slave04 Outlet Port43 Name | RW | 32 bytes
26000 | Slave04 Outlet Port44 Name | RW | 32 bytes
26016 | Slave04 Outlet Port45 Name | RW | 32 bytes
26032 | Slave04 Outlet Port46 Name | RW | 32 bytes
26048 | Slave04 Outlet Port47 Name | RW | 32 bytes
26064 | Slave04 Outlet Port48 Name | RW | 32 bytes
26080 | Slave05 Outlet Port01 Name | RW | 32 bytes
26096 | Slave05 Outlet Port02 Name | RW | 32 bytes
26112 | Slave05 Outlet Port03 Name | RW | 32 bytes
26128 | Slave05 Outlet Port04 Name | RW | 32 bytes
26144 | Slave05 Outlet Port05 Name | RW | 32 bytes
26160 | Slave05 Outlet Port06 Name | RW | 32 bytes
26176 | Slave05 Outlet Port07 Name | RW | 32 bytes
26192 | Slave05 Outlet Port08 Name | RW | 32 bytes
26208 | Slave05 Outlet Port09 Name | RW | 32 bytes
26224 | Slave05 Outlet Port10 Name | RW | 32 bytes
26240 | Slave05 Outlet Port11 Name | RW | 32 bytes
26256 | Slave05 Outlet Port12 Name | RW | 32 bytes
26272 | Slave05 Outlet Port13 Name | RW | 32 bytes
26288 | Slave05 Outlet Port14 Name | RW | 32 bytes
26304 | Slave05 Outlet Port15 Name | RW | 32 bytes
26320 | Slave05 Outlet Port16 Name | RW | 32 bytes
26336 | Slave05 Outlet Port17 Name | RW | 32 bytes
26352 | Slave05 Outlet Port18 Name | RW | 32 bytes
26368 | Slave05 Outlet Port19 Name | RW | 32 bytes
26384 | Slave05 Outlet Port20 Name | RW | 32 bytes
26400 | Slave05 Outlet Port21 Name | RW | 32 bytes
26416 | Slave05 Outlet Port22 Name | RW | 32 bytes
26432 | Slave05 Outlet Port23 Name | RW | 32 bytes
26448 | Slave05 Outlet Port24 Name | RW | 32 bytes
26464 | Slave05 Outlet Port25 Name | RW | 32 bytes
26480 | Slave05 Outlet Port26 Name | RW | 32 bytes
26496 | Slave05 Outlet Port27 Name | RW | 32 bytes
26512 | Slave05 Outlet Port28 Name | RW | 32 bytes
26528 | Slave05 Outlet Port29 Name | RW | 32 bytes
26544 | Slave05 Outlet Port30 Name | RW | 32 bytes
26560 | Slave05 Outlet Port31 Name | RW | 32 bytes
26576 | Slave05 Outlet Port32 Name | RW | 32 bytes
26592 | Slave05 Outlet Port33 Name | RW | 32 bytes
26608 | Slave05 Outlet Port34 Name | RW | 32 bytes
26624 | Slave05 Outlet Port35 Name | RW | 32 bytes
26640 | Slave05 Outlet Port36 Name | RW | 32 bytes
26656 | Slave05 Outlet Port37 Name | RW | 32 bytes
26672 | Slave05 Outlet Port38 Name | RW | 32 bytes
26688 | Slave05 Outlet Port39 Name | RW | 32 bytes
26704 | Slave05 Outlet Port40 Name | RW | 32 bytes
26720 | Slave05 Outlet Port41 Name | RW | 32 bytes
26736 | Slave05 Outlet Port42 Name | RW | 32 bytes
26752 | Slave05 Outlet Port43 Name | RW | 32 bytes
26768 | Slave05 Outlet Port44 Name | RW | 32 bytes
26784 | Slave05 Outlet Port45 Name | RW | 32 bytes
26800 | Slave05 Outlet Port46 Name | RW | 32 bytes
26816 | Slave05 Outlet Port47 Name | RW | 32 bytes
26832 | Slave05 Outlet Port48 Name | RW | 32 bytes
26848 | Slave06 Outlet Port01 Name | RW | 32 bytes
26864 | Slave06 Outlet Port02 Name | RW | 32 bytes
26880 | Slave06 Outlet Port03 Name | RW | 32 bytes
26896 | Slave06 Outlet Port04 Name | RW | 32 bytes
26912 | Slave06 Outlet Port05 Name | RW | 32 bytes
26928 | Slave06 Outlet Port06 Name | RW | 32 bytes
26944 | Slave06 Outlet Port07 Name | RW | 32 bytes
26960 | Slave06 Outlet Port08 Name | RW | 32 bytes
26976 | Slave06 Outlet Port09 Name | RW | 32 bytes
26992 | Slave06 Outlet Port10 Name | RW | 32 bytes
27008 | Slave06 Outlet Port11 Name | RW | 32 bytes
27024 | Slave06 Outlet Port12 Name | RW | 32 bytes
27040 | Slave06 Outlet Port13 Name | RW | 32 bytes
27056 | Slave06 Outlet Port14 Name | RW | 32 bytes
27072 | Slave06 Outlet Port15 Name | RW | 32 bytes
27088 | Slave06 Outlet Port16 Name | RW | 32 bytes
27104 | Slave06 Outlet Port17 Name | RW | 32 bytes
27120 | Slave06 Outlet Port18 Name | RW | 32 bytes
27136 | Slave06 Outlet Port19 Name | RW | 32 bytes
27152 | Slave06 Outlet Port20 Name | RW | 32 bytes
27168 | Slave06 Outlet Port21 Name | RW | 32 bytes
27184 | Slave06 Outlet Port22 Name | RW | 32 bytes
27200 | Slave06 Outlet Port23 Name | RW | 32 bytes
27216 | Slave06 Outlet Port24 Name | RW | 32 bytes
27232 | Slave06 Outlet Port25 Name | RW | 32 bytes
27248 | Slave06 Outlet Port26 Name | RW | 32 bytes
27264 | Slave06 Outlet Port27 Name | RW | 32 bytes
27280 | Slave06 Outlet Port28 Name | RW | 32 bytes
27296 | Slave06 Outlet Port29 Name | RW | 32 bytes
27312 | Slave06 Outlet Port30 Name | RW | 32 bytes
27328 | Slave06 Outlet Port31 Name | RW | 32 bytes
27344 | Slave06 Outlet Port32 Name | RW | 32 bytes
27360 | Slave06 Outlet Port33 Name | RW | 32 bytes
27376 | Slave06 Outlet Port34 Name | RW | 32 bytes
27392 | Slave06 Outlet Port35 Name | RW | 32 bytes
27408 | Slave06 Outlet Port36 Name | RW | 32 bytes
27424 | Slave06 Outlet Port37 Name | RW | 32 bytes
27440 | Slave06 Outlet Port38 Name | RW | 32 bytes
27456 | Slave06 Outlet Port39 Name | RW | 32 bytes
27472 | Slave06 Outlet Port40 Name | RW | 32 bytes
27488 | Slave06 Outlet Port41 Name | RW | 32 bytes
27504 | Slave06 Outlet Port42 Name | RW | 32 bytes
27520 | Slave06 Outlet Port43 Name | RW | 32 bytes
27536 | Slave06 Outlet Port44 Name | RW | 32 bytes
27552 | Slave06 Outlet Port45 Name | RW | 32 bytes
27568 | Slave06 Outlet Port46 Name | RW | 32 bytes
27584 | Slave06 Outlet Port47 Name | RW | 32 bytes
27600 | Slave06 Outlet Port48 Name | RW | 32 bytes
27616 | Slave07 Outlet Port01 Name | RW | 32 bytes
27632 | Slave07 Outlet Port02 Name | RW | 32 bytes
27648 | Slave07 Outlet Port03 Name | RW | 32 bytes
27664 | Slave07 Outlet Port04 Name | RW | 32 bytes
27680 | Slave07 Outlet Port05 Name | RW | 32 bytes
27696 | Slave07 Outlet Port06 Name | RW | 32 bytes
27712 | Slave07 Outlet Port07 Name | RW | 32 bytes
27728 | Slave07 Outlet Port08 Name | RW | 32 bytes
27744 | Slave07 Outlet Port09 Name | RW | 32 bytes
27760 | Slave07 Outlet Port10 Name | RW | 32 bytes
27776 | Slave07 Outlet Port11 Name | RW | 32 bytes
27792 | Slave07 Outlet Port12 Name | RW | 32 bytes
27808 | Slave07 Outlet Port13 Name | RW | 32 bytes
27824 | Slave07 Outlet Port14 Name | RW | 32 bytes
27840 | Slave07 Outlet Port15 Name | RW | 32 bytes
27856 | Slave07 Outlet Port16 Name | RW | 32 bytes
27872 | Slave07 Outlet Port17 Name | RW | 32 bytes
27888 | Slave07 Outlet Port18 Name | RW | 32 bytes
27904 | Slave07 Outlet Port19 Name | RW | 32 bytes
27920 | Slave07 Outlet Port20 Name | RW | 32 bytes
27936 | Slave07 Outlet Port21 Name | RW | 32 bytes
27952 | Slave07 Outlet Port22 Name | RW | 32 bytes
27968 | Slave07 Outlet Port23 Name | RW | 32 bytes
27984 | Slave07 Outlet Port24 Name | RW | 32 bytes
28000 | Slave07 Outlet Port25 Name | RW | 32 bytes
28016 | Slave07 Outlet Port26 Name | RW | 32 bytes
28032 | Slave07 Outlet Port27 Name | RW | 32 bytes
28048 | Slave07 Outlet Port28 Name | RW | 32 bytes
28064 | Slave07 Outlet Port29 Name | RW | 32 bytes
28080 | Slave07 Outlet Port30 Name | RW | 32 bytes
28096 | Slave07 Outlet Port31 Name | RW | 32 bytes
28112 | Slave07 Outlet Port32 Name | RW | 32 bytes
28128 | Slave07 Outlet Port33 Name | RW | 32 bytes
28144 | Slave07 Outlet Port34 Name | RW | 32 bytes
28160 | Slave07 Outlet Port35 Name | RW | 32 bytes
28176 | Slave07 Outlet Port36 Name | RW | 32 bytes
28192 | Slave07 Outlet Port37 Name | RW | 32 bytes
28208 | Slave07 Outlet Port38 Name | RW | 32 bytes
28224 | Slave07 Outlet Port39 Name | RW | 32 bytes
28240 | Slave07 Outlet Port40 Name | RW | 32 bytes
28256 | Slave07 Outlet Port41 Name | RW | 32 bytes
28272 | Slave07 Outlet Port42 Name | RW | 32 bytes
28288 | Slave07 Outlet Port43 Name | RW | 32 bytes
28304 | Slave07 Outlet Port44 Name | RW | 32 bytes
28320 | Slave07 Outlet Port45 Name | RW | 32 bytes
28336 | Slave07 Outlet Port46 Name | RW | 32 bytes
28352 | Slave07 Outlet Port47 Name | RW | 32 bytes
28368 | Slave07 Outlet Port48 Name | RW | 32 bytes
28384 | Slave08 Outlet Port01 Name | RW | 32 bytes
28400 | Slave08 Outlet Port02 Name | RW | 32 bytes
28416 | Slave08 Outlet Port03 Name | RW | 32 bytes
28432 | Slave08 Outlet Port04 Name | RW | 32 bytes
28448 | Slave08 Outlet Port05 Name | RW | 32 bytes
28464 | Slave08 Outlet Port06 Name | RW | 32 bytes
28480 | Slave08 Outlet Port07 Name | RW | 32 bytes
28496 | Slave08 Outlet Port08 Name | RW | 32 bytes
28512 | Slave08 Outlet Port09 Name | RW | 32 bytes
28528 | Slave08 Outlet Port10 Name | RW | 32 bytes
28544 | Slave08 Outlet Port11 Name | RW | 32 bytes
28560 | Slave08 Outlet Port12 Name | RW | 32 bytes
28576 | Slave08 Outlet Port13 Name | RW | 32 bytes
28592 | Slave08 Outlet Port14 Name | RW | 32 bytes
28608 | Slave08 Outlet Port15 Name | RW | 32 bytes
28624 | Slave08 Outlet Port16 Name | RW | 32 bytes
28640 | Slave08 Outlet Port17 Name | RW | 32 bytes
28656 | Slave08 Outlet Port18 Name | RW | 32 bytes
28672 | Slave08 Outlet Port19 Name | RW | 32 bytes
28688 | Slave08 Outlet Port20 Name | RW | 32 bytes
28704 | Slave08 Outlet Port21 Name | RW | 32 bytes
28720 | Slave08 Outlet Port22 Name | RW | 32 bytes
28736 | Slave08 Outlet Port23 Name | RW | 32 bytes
28752 | Slave08 Outlet Port24 Name | RW | 32 bytes
28768 | Slave08 Outlet Port25 Name | RW | 32 bytes
28784 | Slave08 Outlet Port26 Name | RW | 32 bytes
28800 | Slave08 Outlet Port27 Name | RW | 32 bytes
28816 | Slave08 Outlet Port28 Name | RW | 32 bytes
28832 | Slave08 Outlet Port29 Name | RW | 32 bytes
28848 | Slave08 Outlet Port30 Name | RW | 32 bytes
28864 | Slave08 Outlet Port31 Name | RW | 32 bytes
28880 | Slave08 Outlet Port32 Name | RW | 32 bytes
28896 | Slave08 Outlet Port33 Name | RW | 32 bytes
28912 | Slave08 Outlet Port34 Name | RW | 32 bytes
28928 | Slave08 Outlet Port35 Name | RW | 32 bytes
28944 | Slave08 Outlet Port36 Name | RW | 32 bytes
28960 | Slave08 Outlet Port37 Name | RW | 32 bytes
28976 | Slave08 Outlet Port38 Name | RW | 32 bytes
28992 | Slave08 Outlet Port39 Name | RW | 32 bytes
29008 | Slave08 Outlet Port40 Name | RW | 32 bytes
29024 | Slave08 Outlet Port41 Name | RW | 32 bytes
29040 | Slave08 Outlet Port42 Name | RW | 32 bytes
29056 | Slave08 Outlet Port43 Name | RW | 32 bytes
29072 | Slave08 Outlet Port44 Name | RW | 32 bytes
29088 | Slave08 Outlet Port45 Name | RW | 32 bytes
29104 | Slave08 Outlet Port46 Name | RW | 32 bytes
29120 | Slave08 Outlet Port47 Name | RW | 32 bytes
29136 | Slave08 Outlet Port48 Name | RW | 32 bytes
29152 | Slave09 Outlet Port01 Name | RW | 32 bytes
29168 | Slave09 Outlet Port02 Name | RW | 32 bytes
29184 | Slave09 Outlet Port03 Name | RW | 32 bytes
29200 | Slave09 Outlet Port04 Name | RW | 32 bytes
29216 | Slave09 Outlet Port05 Name | RW | 32 bytes
29232 | Slave09 Outlet Port06 Name | RW | 32 bytes
29248 | Slave09 Outlet Port07 Name | RW | 32 bytes
29264 | Slave09 Outlet Port08 Name | RW | 32 bytes
29280 | Slave09 Outlet Port09 Name | RW | 32 bytes
29296 | Slave09 Outlet Port10 Name | RW | 32 bytes
29312 | Slave09 Outlet Port11 Name | RW | 32 bytes
29328 | Slave09 Outlet Port12 Name | RW | 32 bytes
29344 | Slave09 Outlet Port13 Name | RW | 32 bytes
29360 | Slave09 Outlet Port14 Name | RW | 32 bytes
29376 | Slave09 Outlet Port15 Name | RW | 32 bytes
29392 | Slave09 Outlet Port16 Name | RW | 32 bytes
29408 | Slave09 Outlet Port17 Name | RW | 32 bytes
29424 | Slave09 Outlet Port18 Name | RW | 32 bytes
29440 | Slave09 Outlet Port19 Name | RW | 32 bytes
29456 | Slave09 Outlet Port20 Name | RW | 32 bytes
29472 | Slave09 Outlet Port21 Name | RW | 32 bytes
29488 | Slave09 Outlet Port22 Name | RW | 32 bytes
29504 | Slave09 Outlet Port23 Name | RW | 32 bytes
29520 | Slave09 Outlet Port24 Name | RW | 32 bytes
29536 | Slave09 Outlet Port25 Name | RW | 32 bytes
29552 | Slave09 Outlet Port26 Name | RW | 32 bytes
29568 | Slave09 Outlet Port27 Name | RW | 32 bytes
29584 | Slave09 Outlet Port28 Name | RW | 32 bytes
29600 | Slave09 Outlet Port29 Name | RW | 32 bytes
29616 | Slave09 Outlet Port30 Name | RW | 32 bytes
29632 | Slave09 Outlet Port31 Name | RW | 32 bytes
29648 | Slave09 Outlet Port32 Name | RW | 32 bytes
29664 | Slave09 Outlet Port33 Name | RW | 32 bytes
29680 | Slave09 Outlet Port34 Name | RW | 32 bytes
29696 | Slave09 Outlet Port35 Name | RW | 32 bytes
29712 | Slave09 Outlet Port36 Name | RW | 32 bytes
29728 | Slave09 Outlet Port37 Name | RW | 32 bytes
29744 | Slave09 Outlet Port38 Name | RW | 32 bytes
29760 | Slave09 Outlet Port39 Name | RW | 32 bytes
29776 | Slave09 Outlet Port40 Name | RW | 32 bytes
29792 | Slave09 Outlet Port41 Name | RW | 32 bytes
29808 | Slave09 Outlet Port42 Name | RW | 32 bytes
29824 | Slave09 Outlet Port43 Name | RW | 32 bytes
29840 | Slave09 Outlet Port44 Name | RW | 32 bytes
29856 | Slave09 Outlet Port45 Name | RW | 32 bytes
29872 | Slave09 Outlet Port46 Name | RW | 32 bytes
29888 | Slave09 Outlet Port47 Name | RW | 32 bytes
29904 | Slave09 Outlet Port48 Name | RW | 32 bytes
29920 | Slave10 Outlet Port01 Name | RW | 32 bytes
29936 | Slave10 Outlet Port02 Name | RW | 32 bytes
29952 | Slave10 Outlet Port03 Name | RW | 32 bytes
29968 | Slave10 Outlet Port04 Name | RW | 32 bytes
29984 | Slave10 Outlet Port05 Name | RW | 32 bytes
30000 | Slave10 Outlet Port06 Name | RW | 32 bytes
30016 | Slave10 Outlet Port07 Name | RW | 32 bytes
30032 | Slave10 Outlet Port08 Name | RW | 32 bytes
30048 | Slave10 Outlet Port09 Name | RW | 32 bytes
30064 | Slave10 Outlet Port10 Name | RW | 32 bytes
30080 | Slave10 Outlet Port11 Name | RW | 32 bytes
30096 | Slave10 Outlet Port12 Name | RW | 32 bytes
30112 | Slave10 Outlet Port13 Name | RW | 32 bytes
30128 | Slave10 Outlet Port14 Name | RW | 32 bytes
30144 | Slave10 Outlet Port15 Name | RW | 32 bytes
30160 | Slave10 Outlet Port16 Name | RW | 32 bytes
30176 | Slave10 Outlet Port17 Name | RW | 32 bytes
30192 | Slave10 Outlet Port18 Name | RW | 32 bytes
30208 | Slave10 Outlet Port19 Name | RW | 32 bytes
30224 | Slave10 Outlet Port20 Name | RW | 32 bytes
30240 | Slave10 Outlet Port21 Name | RW | 32 bytes
30256 | Slave10 Outlet Port22 Name | RW | 32 bytes
30272 | Slave10 Outlet Port23 Name | RW | 32 bytes
30288 | Slave10 Outlet Port24 Name | RW | 32 bytes
30304 | Slave10 Outlet Port25 Name | RW | 32 bytes
30320 | Slave10 Outlet Port26 Name | RW | 32 bytes
30336 | Slave10 Outlet Port27 Name | RW | 32 bytes
30352 | Slave10 Outlet Port28 Name | RW | 32 bytes
30368 | Slave10 Outlet Port29 Name | RW | 32 bytes
30384 | Slave10 Outlet Port30 Name | RW | 32 bytes
30400 | Slave10 Outlet Port31 Name | RW | 32 bytes
30416 | Slave10 Outlet Port32 Name | RW | 32 bytes
30432 | Slave10 Outlet Port33 Name | RW | 32 bytes
30448 | Slave10 Outlet Port34 Name | RW | 32 bytes
30464 | Slave10 Outlet Port35 Name | RW | 32 bytes
30480 | Slave10 Outlet Port36 Name | RW | 32 bytes
30496 | Slave10 Outlet Port37 Name | RW | 32 bytes
30512 | Slave10 Outlet Port38 Name | RW | 32 bytes
30528 | Slave10 Outlet Port39 Name | RW | 32 bytes
30544 | Slave10 Outlet Port40 Name | RW | 32 bytes
30560 | Slave10 Outlet Port41 Name | RW | 32 bytes
30576 | Slave10 Outlet Port42 Name | RW | 32 bytes
30592 | Slave10 Outlet Port43 Name | RW | 32 bytes
30608 | Slave10 Outlet Port44 Name | RW | 32 bytes
30624 | Slave10 Outlet Port45 Name | RW | 32 bytes
30640 | Slave10 Outlet Port46 Name | RW | 32 bytes
30656 | Slave10 Outlet Port47 Name | RW | 32 bytes
30672 | Slave10 Outlet Port48 Name | RW | 32 bytes
30688 | Slave11 Outlet Port01 Name | RW | 32 bytes
30704 | Slave11 Outlet Port02 Name | RW | 32 bytes
30720 | Slave11 Outlet Port03 Name | RW | 32 bytes
30736 | Slave11 Outlet Port04 Name | RW | 32 bytes
30752 | Slave11 Outlet Port05 Name | RW | 32 bytes
30768 | Slave11 Outlet Port06 Name | RW | 32 bytes
30784 | Slave11 Outlet Port07 Name | RW | 32 bytes
30800 | Slave11 Outlet Port08 Name | RW | 32 bytes
30816 | Slave11 Outlet Port09 Name | RW | 32 bytes
30832 | Slave11 Outlet Port10 Name | RW | 32 bytes
30848 | Slave11 Outlet Port11 Name | RW | 32 bytes
30864 | Slave11 Outlet Port12 Name | RW | 32 bytes
30880 | Slave11 Outlet Port13 Name | RW | 32 bytes
30896 | Slave11 Outlet Port14 Name | RW | 32 bytes
30912 | Slave11 Outlet Port15 Name | RW | 32 bytes
30928 | Slave11 Outlet Port16 Name | RW | 32 bytes
30944 | Slave11 Outlet Port17 Name | RW | 32 bytes
30960 | Slave11 Outlet Port18 Name | RW | 32 bytes
30976 | Slave11 Outlet Port19 Name | RW | 32 bytes
30992 | Slave11 Outlet Port20 Name | RW | 32 bytes
31008 | Slave11 Outlet Port21 Name | RW | 32 bytes
31024 | Slave11 Outlet Port22 Name | RW | 32 bytes
31040 | Slave11 Outlet Port23 Name | RW | 32 bytes
31056 | Slave11 Outlet Port24 Name | RW | 32 bytes
31072 | Slave11 Outlet Port25 Name | RW | 32 bytes
31088 | Slave11 Outlet Port26 Name | RW | 32 bytes
31104 | Slave11 Outlet Port27 Name | RW | 32 bytes
31120 | Slave11 Outlet Port28 Name | RW | 32 bytes
31136 | Slave11 Outlet Port29 Name | RW | 32 bytes
31152 | Slave11 Outlet Port30 Name | RW | 32 bytes
31168 | Slave11 Outlet Port31 Name | RW | 32 bytes
31184 | Slave11 Outlet Port32 Name | RW | 32 bytes
31200 | Slave11 Outlet Port33 Name | RW | 32 bytes
31216 | Slave11 Outlet Port34 Name | RW | 32 bytes
31232 | Slave11 Outlet Port35 Name | RW | 32 bytes
31248 | Slave11 Outlet Port36 Name | RW | 32 bytes
31264 | Slave11 Outlet Port37 Name | RW | 32 bytes
31280 | Slave11 Outlet Port38 Name | RW | 32 bytes
31296 | Slave11 Outlet Port39 Name | RW | 32 bytes
31312 | Slave11 Outlet Port40 Name | RW | 32 bytes
31328 | Slave11 Outlet Port41 Name | RW | 32 bytes
31344 | Slave11 Outlet Port42 Name | RW | 32 bytes
31360 | Slave11 Outlet Port43 Name | RW | 32 bytes
31376 | Slave11 Outlet Port44 Name | RW | 32 bytes
31392 | Slave11 Outlet Port45 Name | RW | 32 bytes
31408 | Slave11 Outlet Port46 Name | RW | 32 bytes
31424 | Slave11 Outlet Port47 Name | RW | 32 bytes
31440 | Slave11 Outlet Port48 Name | RW | 32 bytes
31456 | Slave12 Outlet Port01 Name | RW | 32 bytes
31472 | Slave12 Outlet Port02 Name | RW | 32 bytes
31488 | Slave12 Outlet Port03 Name | RW | 32 bytes
31504 | Slave12 Outlet Port04 Name | RW | 32 bytes
31520 | Slave12 Outlet Port05 Name | RW | 32 bytes
31536 | Slave12 Outlet Port06 Name | RW | 32 bytes
31552 | Slave12 Outlet Port07 Name | RW | 32 bytes
31568 | Slave12 Outlet Port08 Name | RW | 32 bytes
31584 | Slave12 Outlet Port09 Name | RW | 32 bytes
31600 | Slave12 Outlet Port10 Name | RW | 32 bytes
31616 | Slave12 Outlet Port11 Name | RW | 32 bytes
31632 | Slave12 Outlet Port12 Name | RW | 32 bytes
31648 | Slave12 Outlet Port13 Name | RW | 32 bytes
31664 | Slave12 Outlet Port14 Name | RW | 32 bytes
31680 | Slave12 Outlet Port15 Name | RW | 32 bytes
31696 | Slave12 Outlet Port16 Name | RW | 32 bytes
31712 | Slave12 Outlet Port17 Name | RW | 32 bytes
31728 | Slave12 Outlet Port18 Name | RW | 32 bytes
31744 | Slave12 Outlet Port19 Name | RW | 32 bytes
31760 | Slave12 Outlet Port20 Name | RW | 32 bytes
31776 | Slave12 Outlet Port21 Name | RW | 32 bytes
31792 | Slave12 Outlet Port22 Name | RW | 32 bytes
31808 | Slave12 Outlet Port23 Name | RW | 32 bytes
31824 | Slave12 Outlet Port24 Name | RW | 32 bytes
31840 | Slave12 Outlet Port25 Name | RW | 32 bytes
31856 | Slave12 Outlet Port26 Name | RW | 32 bytes
31872 | Slave12 Outlet Port27 Name | RW | 32 bytes
31888 | Slave12 Outlet Port28 Name | RW | 32 bytes
31904 | Slave12 Outlet Port29 Name | RW | 32 bytes
31920 | Slave12 Outlet Port30 Name | RW | 32 bytes
31936 | Slave12 Outlet Port31 Name | RW | 32 bytes
31952 | Slave12 Outlet Port32 Name | RW | 32 bytes
31968 | Slave12 Outlet Port33 Name | RW | 32 bytes
31984 | Slave12 Outlet Port34 Name | RW | 32 bytes
32000 | Slave12 Outlet Port35 Name | RW | 32 bytes
32016 | Slave12 Outlet Port36 Name | RW | 32 bytes
32032 | Slave12 Outlet Port37 Name | RW | 32 bytes
32048 | Slave12 Outlet Port38 Name | RW | 32 bytes
32064 | Slave12 Outlet Port39 Name | RW | 32 bytes
32080 | Slave12 Outlet Port40 Name | RW | 32 bytes
32096 | Slave12 Outlet Port41 Name | RW | 32 bytes
32112 | Slave12 Outlet Port42 Name | RW | 32 bytes
32128 | Slave12 Outlet Port43 Name | RW | 32 bytes
32144 | Slave12 Outlet Port44 Name | RW | 32 bytes
32160 | Slave12 Outlet Port45 Name | RW | 32 bytes
32176 | Slave12 Outlet Port46 Name | RW | 32 bytes
32192 | Slave12 Outlet Port47 Name | RW | 32 bytes
32208 | Slave12 Outlet Port48 Name | RW | 32 bytes
32224 | Slave13 Outlet Port01 Name | RW | 32 bytes
32240 | Slave13 Outlet Port02 Name | RW | 32 bytes
32256 | Slave13 Outlet Port03 Name | RW | 32 bytes
32272 | Slave13 Outlet Port04 Name | RW | 32 bytes
32288 | Slave13 Outlet Port05 Name | RW | 32 bytes
32304 | Slave13 Outlet Port06 Name | RW | 32 bytes
32320 | Slave13 Outlet Port07 Name | RW | 32 bytes
32336 | Slave13 Outlet Port08 Name | RW | 32 bytes
32352 | Slave13 Outlet Port09 Name | RW | 32 bytes
32368 | Slave13 Outlet Port10 Name | RW | 32 bytes
32384 | Slave13 Outlet Port11 Name | RW | 32 bytes
32400 | Slave13 Outlet Port12 Name | RW | 32 bytes
32416 | Slave13 Outlet Port13 Name | RW | 32 bytes
32432 | Slave13 Outlet Port14 Name | RW | 32 bytes
32448 | Slave13 Outlet Port15 Name | RW | 32 bytes
32464 | Slave13 Outlet Port16 Name | RW | 32 bytes
32480 | Slave13 Outlet Port17 Name | RW | 32 bytes
32496 | Slave13 Outlet Port18 Name | RW | 32 bytes
32512 | Slave13 Outlet Port19 Name | RW | 32 bytes
32528 | Slave13 Outlet Port20 Name | RW | 32 bytes
32544 | Slave13 Outlet Port21 Name | RW | 32 bytes
32560 | Slave13 Outlet Port22 Name | RW | 32 bytes
32576 | Slave13 Outlet Port23 Name | RW | 32 bytes
32592 | Slave13 Outlet Port24 Name | RW | 32 bytes
32608 | Slave13 Outlet Port25 Name | RW | 32 bytes
32624 | Slave13 Outlet Port26 Name | RW | 32 bytes
32640 | Slave13 Outlet Port27 Name | RW | 32 bytes
32656 | Slave13 Outlet Port28 Name | RW | 32 bytes
32672 | Slave13 Outlet Port29 Name | RW | 32 bytes
32688 | Slave13 Outlet Port30 Name | RW | 32 bytes
32704 | Slave13 Outlet Port31 Name | RW | 32 bytes
32720 | Slave13 Outlet Port32 Name | RW | 32 bytes
32736 | Slave13 Outlet Port33 Name | RW | 32 bytes
32752 | Slave13 Outlet Port34 Name | RW | 32 bytes
32768 | Slave13 Outlet Port35 Name | RW | 32 bytes
32784 | Slave13 Outlet Port36 Name | RW | 32 bytes
32800 | Slave13 Outlet Port37 Name | RW | 32 bytes
32816 | Slave13 Outlet Port38 Name | RW | 32 bytes
32832 | Slave13 Outlet Port39 Name | RW | 32 bytes
32848 | Slave13 Outlet Port40 Name | RW | 32 bytes
32864 | Slave13 Outlet Port41 Name | RW | 32 bytes
32880 | Slave13 Outlet Port42 Name | RW | 32 bytes
32896 | Slave13 Outlet Port43 Name | RW | 32 bytes
32912 | Slave13 Outlet Port44 Name | RW | 32 bytes
32928 | Slave13 Outlet Port45 Name | RW | 32 bytes
32944 | Slave13 Outlet Port46 Name | RW | 32 bytes
32960 | Slave13 Outlet Port47 Name | RW | 32 bytes
32976 | Slave13 Outlet Port48 Name | RW | 32 bytes
32992 | Slave14 Outlet Port01 Name | RW | 32 bytes
33008 | Slave14 Outlet Port02 Name | RW | 32 bytes
33024 | Slave14 Outlet Port03 Name | RW | 32 bytes
33040 | Slave14 Outlet Port04 Name | RW | 32 bytes
33056 | Slave14 Outlet Port05 Name | RW | 32 bytes
33072 | Slave14 Outlet Port06 Name | RW | 32 bytes
33088 | Slave14 Outlet Port07 Name | RW | 32 bytes
33104 | Slave14 Outlet Port08 Name | RW | 32 bytes
33120 | Slave14 Outlet Port09 Name | RW | 32 bytes
33136 | Slave14 Outlet Port10 Name | RW | 32 bytes
33152 | Slave14 Outlet Port11 Name | RW | 32 bytes
33168 | Slave14 Outlet Port12 Name | RW | 32 bytes
33184 | Slave14 Outlet Port13 Name | RW | 32 bytes
33200 | Slave14 Outlet Port14 Name | RW | 32 bytes
33216 | Slave14 Outlet Port15 Name | RW | 32 bytes
33232 | Slave14 Outlet Port16 Name | RW | 32 bytes
33248 | Slave14 Outlet Port17 Name | RW | 32 bytes
33264 | Slave14 Outlet Port18 Name | RW | 32 bytes
33280 | Slave14 Outlet Port19 Name | RW | 32 bytes
33296 | Slave14 Outlet Port20 Name | RW | 32 bytes
33312 | Slave14 Outlet Port21 Name | RW | 32 bytes
33328 | Slave14 Outlet Port22 Name | RW | 32 bytes
33344 | Slave14 Outlet Port23 Name | RW | 32 bytes
33360 | Slave14 Outlet Port24 Name | RW | 32 bytes
33376 | Slave14 Outlet Port25 Name | RW | 32 bytes
33392 | Slave14 Outlet Port26 Name | RW | 32 bytes
33408 | Slave14 Outlet Port27 Name | RW | 32 bytes
33424 | Slave14 Outlet Port28 Name | RW | 32 bytes
33440 | Slave14 Outlet Port29 Name | RW | 32 bytes
33456 | Slave14 Outlet Port30 Name | RW | 32 bytes
33472 | Slave14 Outlet Port31 Name | RW | 32 bytes
33488 | Slave14 Outlet Port32 Name | RW | 32 bytes
33504 | Slave14 Outlet Port33 Name | RW | 32 bytes
33520 | Slave14 Outlet Port34 Name | RW | 32 bytes
33536 | Slave14 Outlet Port35 Name | RW | 32 bytes
33552 | Slave14 Outlet Port36 Name | RW | 32 bytes
33568 | Slave14 Outlet Port37 Name | RW | 32 bytes
33584 | Slave14 Outlet Port38 Name | RW | 32 bytes
33600 | Slave14 Outlet Port39 Name | RW | 32 bytes
33616 | Slave14 Outlet Port40 Name | RW | 32 bytes
33632 | Slave14 Outlet Port41 Name | RW | 32 bytes
33648 | Slave14 Outlet Port42 Name | RW | 32 bytes
33664 | Slave14 Outlet Port43 Name | RW | 32 bytes
33680 | Slave14 Outlet Port44 Name | RW | 32 bytes
33696 | Slave14 Outlet Port45 Name | RW | 32 bytes
33712 | Slave14 Outlet Port46 Name | RW | 32 bytes
33728 | Slave14 Outlet Port47 Name | RW | 32 bytes
33744 | Slave14 Outlet Port48 Name | RW | 32 bytes
33760 | Slave15 Outlet Port01 Name | RW | 32 bytes
33776 | Slave15 Outlet Port02 Name | RW | 32 bytes
33792 | Slave15 Outlet Port03 Name | RW | 32 bytes
33808 | Slave15 Outlet Port04 Name | RW | 32 bytes
33824 | Slave15 Outlet Port05 Name | RW | 32 bytes
33840 | Slave15 Outlet Port06 Name | RW | 32 bytes
33856 | Slave15 Outlet Port07 Name | RW | 32 bytes
33872 | Slave15 Outlet Port08 Name | RW | 32 bytes
33888 | Slave15 Outlet Port09 Name | RW | 32 bytes
33904 | Slave15 Outlet Port10 Name | RW | 32 bytes
33920 | Slave15 Outlet Port11 Name | RW | 32 bytes
33936 | Slave15 Outlet Port12 Name | RW | 32 bytes
33952 | Slave15 Outlet Port13 Name | RW | 32 bytes
33968 | Slave15 Outlet Port14 Name | RW | 32 bytes
33984 | Slave15 Outlet Port15 Name | RW | 32 bytes
34000 | Slave15 Outlet Port16 Name | RW | 32 bytes
34016 | Slave15 Outlet Port17 Name | RW | 32 bytes
34032 | Slave15 Outlet Port18 Name | RW | 32 bytes
34048 | Slave15 Outlet Port19 Name | RW | 32 bytes
34064 | Slave15 Outlet Port20 Name | RW | 32 bytes
34080 | Slave15 Outlet Port21 Name | RW | 32 bytes
34096 | Slave15 Outlet Port22 Name | RW | 32 bytes
34112 | Slave15 Outlet Port23 Name | RW | 32 bytes
34128 | Slave15 Outlet Port24 Name | RW | 32 bytes
34144 | Slave15 Outlet Port25 Name | RW | 32 bytes
34160 | Slave15 Outlet Port26 Name | RW | 32 bytes
34176 | Slave15 Outlet Port27 Name | RW | 32 bytes
34192 | Slave15 Outlet Port28 Name | RW | 32 bytes
34208 | Slave15 Outlet Port29 Name | RW | 32 bytes
34224 | Slave15 Outlet Port30 Name | RW | 32 bytes
34240 | Slave15 Outlet Port31 Name | RW | 32 bytes
34256 | Slave15 Outlet Port32 Name | RW | 32 bytes
34272 | Slave15 Outlet Port33 Name | RW | 32 bytes
34288 | Slave15 Outlet Port34 Name | RW | 32 bytes
34304 | Slave15 Outlet Port35 Name | RW | 32 bytes
34320 | Slave15 Outlet Port36 Name | RW | 32 bytes
34336 | Slave15 Outlet Port37 Name | RW | 32 bytes
34352 | Slave15 Outlet Port38 Name | RW | 32 bytes
34368 | Slave15 Outlet Port39 Name | RW | 32 bytes
34384 | Slave15 Outlet Port40 Name | RW | 32 bytes
34400 | Slave15 Outlet Port41 Name | RW | 32 bytes
34416 | Slave15 Outlet Port42 Name | RW | 32 bytes
34432 | Slave15 Outlet Port43 Name | RW | 32 bytes
34448 | Slave15 Outlet Port44 Name | RW | 32 bytes
34464 | Slave15 Outlet Port45 Name | RW | 32 bytes
34480 | Slave15 Outlet Port46 Name | RW | 32 bytes
34496 | Slave15 Outlet Port47 Name | RW | 32 bytes
34512 | Slave15 Outlet Port48 Name | RW | 32 bytes
34528 | Master EMD-1 Name | RW | 32 bytes
34544 | Master EMD-2 Name | RW | 32 bytes
34560 | Master EMD-3 Name | RW | 32 bytes
34576 | Master EMD-4 Name | RW | 32 bytes
34592 | Master EMD-5 Name | RW | 32 bytes
34608 | Master EMD-6 Name | RW | 32 bytes
34624 | Master EMD-7 Name | RW | 32 bytes
34640 | Master EMD-8 Name | RW | 32 bytes
34656 | Slave01 EMD-1 Name | RW | 32 bytes
34672 | Slave01 EMD-2 Name | RW | 32 bytes
34688 | Slave01 EMD-3 Name | RW | 32 bytes
34704 | Slave01 EMD-4 Name | RW | 32 bytes
34720 | Slave01 EMD-5 Name | RW | 32 bytes
34736 | Slave01 EMD-6 Name | RW | 32 bytes
34752 | Slave01 EMD-7 Name | RW | 32 bytes
34768 | Slave01 EMD-8 Name | RW | 32 bytes
34784 | Slave02 EMD-1 Name | RW | 32 bytes
34800 | Slave02 EMD-2 Name | RW | 32 bytes
34816 | Slave02 EMD-3 Name | RW | 32 bytes
34832 | Slave02 EMD-4 Name | RW | 32 bytes
34848 | Slave02 EMD-5 Name | RW | 32 bytes
34864 | Slave02 EMD-6 Name | RW | 32 bytes
34880 | Slave02 EMD-7 Name | RW | 32 bytes
34896 | Slave02 EMD-8 Name | RW | 32 bytes
34912 | Slave03 EMD-1 Name | RW | 32 bytes
34928 | Slave03 EMD-2 Name | RW | 32 bytes
34944 | Slave03 EMD-3 Name | RW | 32 bytes
34960 | Slave03 EMD-4 Name | RW | 32 bytes
34976 | Slave03 EMD-5 Name | RW | 32 bytes
34992 | Slave03 EMD-6 Name | RW | 32 bytes
35008 | Slave03 EMD-7 Name | RW | 32 bytes
35024 | Slave03 EMD-8 Name | RW | 32 bytes
35040 | Slave04 EMD-1 Name | RW | 32 bytes
35056 | Slave04 EMD-2 Name | RW | 32 bytes
35072 | Slave04 EMD-3 Name | RW | 32 bytes
35088 | Slave04 EMD-4 Name | RW | 32 bytes
35104 | Slave04 EMD-5 Name | RW | 32 bytes
35120 | Slave04 EMD-6 Name | RW | 32 bytes
35136 | Slave04 EMD-7 Name | RW | 32 bytes
35152 | Slave04 EMD-8 Name | RW | 32 bytes
35168 | Slave05 EMD-1 Name | RW | 32 bytes
35184 | Slave05 EMD-2 Name | RW | 32 bytes
35200 | Slave05 EMD-3 Name | RW | 32 bytes
35216 | Slave05 EMD-4 Name | RW | 32 bytes
35232 | Slave05 EMD-5 Name | RW | 32 bytes
35248 | Slave05 EMD-6 Name | RW | 32 bytes
35264 | Slave05 EMD-7 Name | RW | 32 bytes
35280 | Slave05 EMD-8 Name | RW | 32 bytes
35296 | Slave06 EMD-1 Name | RW | 32 bytes
35312 | Slave06 EMD-2 Name | RW | 32 bytes
35328 | Slave06 EMD-3 Name | RW | 32 bytes
35344 | Slave06 EMD-4 Name | RW | 32 bytes
35360 | Slave06 EMD-5 Name | RW | 32 bytes
35376 | Slave06 EMD-6 Name | RW | 32 bytes
35392 | Slave06 EMD-7 Name | RW | 32 bytes
35408 | Slave06 EMD-8 Name | RW | 32 bytes
35424 | Slave07 EMD-1 Name | RW | 32 bytes
35440 | Slave07 EMD-2 Name | RW | 32 bytes
35456 | Slave07 EMD-3 Name | RW | 32 bytes
35472 | Slave07 EMD-4 Name | RW | 32 bytes
35488 | Slave07 EMD-5 Name | RW | 32 bytes
35504 | Slave07 EMD-6 Name | RW | 32 bytes
35520 | Slave07 EMD-7 Name | RW | 32 bytes
35536 | Slave07 EMD-8 Name | RW | 32 bytes
35552 | Slave08 EMD-1 Name | RW | 32 bytes
35568 | Slave08 EMD-2 Name | RW | 32 bytes
35584 | Slave08 EMD-3 Name | RW | 32 bytes
35600 | Slave08 EMD-4 Name | RW | 32 bytes
35616 | Slave08 EMD-5 Name | RW | 32 bytes
35632 | Slave08 EMD-6 Name | RW | 32 bytes
35648 | Slave08 EMD-7 Name | RW | 32 bytes
35664 | Slave08 EMD-8 Name | RW | 32 bytes
35680 | Slave09 EMD-1 Name | RW | 32 bytes
35696 | Slave09 EMD-2 Name | RW | 32 bytes
35712 | Slave09 EMD-3 Name | RW | 32 bytes
35728 | Slave09 EMD-4 Name | RW | 32 bytes
35744 | Slave09 EMD-5 Name | RW | 32 bytes
35760 | Slave09 EMD-6 Name | RW | 32 bytes
35776 | Slave09 EMD-7 Name | RW | 32 bytes
35792 | Slave09 EMD-8 Name | RW | 32 bytes
35808 | Slave10 EMD-1 Name | RW | 32 bytes
35824 | Slave10 EMD-2 Name | RW | 32 bytes
35840 | Slave10 EMD-3 Name | RW | 32 bytes
35856 | Slave10 EMD-4 Name | RW | 32 bytes
35872 | Slave10 EMD-5 Name | RW | 32 bytes
35888 | Slave10 EMD-6 Name | RW | 32 bytes
35904 | Slave10 EMD-7 Name | RW | 32 bytes
35920 | Slave10 EMD-8 Name | RW | 32 bytes
35936 | Slave11 EMD-1 Name | RW | 32 bytes
35952 | Slave11 EMD-2 Name | RW | 32 bytes
35968 | Slave11 EMD-3 Name | RW | 32 bytes
35984 | Slave11 EMD-4 Name | RW | 32 bytes
36000 | Slave11 EMD-5 Name | RW | 32 bytes
36016 | Slave11 EMD-6 Name | RW | 32 bytes
36032 | Slave11 EMD-7 Name | RW | 32 bytes
36048 | Slave11 EMD-8 Name | RW | 32 bytes
36064 | Slave12 EMD-1 Name | RW | 32 bytes
36080 | Slave12 EMD-2 Name | RW | 32 bytes
36096 | Slave12 EMD-3 Name | RW | 32 bytes
36112 | Slave12 EMD-4 Name | RW | 32 bytes
36128 | Slave12 EMD-5 Name | RW | 32 bytes
36144 | Slave12 EMD-6 Name | RW | 32 bytes
36160 | Slave12 EMD-7 Name | RW | 32 bytes
36176 | Slave12 EMD-8 Name | RW | 32 bytes
36192 | Slave13 EMD-1 Name | RW | 32 bytes
36208 | Slave13 EMD-2 Name | RW | 32 bytes
36224 | Slave13 EMD-3 Name | RW | 32 bytes
36240 | Slave13 EMD-4 Name | RW | 32 bytes
36256 | Slave13 EMD-5 Name | RW | 32 bytes
36272 | Slave13 EMD-6 Name | RW | 32 bytes
36288 | Slave13 EMD-7 Name | RW | 32 bytes
36304 | Slave13 EMD-8 Name | RW | 32 bytes
36320 | Slave14 EMD-1 Name | RW | 32 bytes
36336 | Slave14 EMD-2 Name | RW | 32 bytes
36352 | Slave14 EMD-3 Name | RW | 32 bytes
36368 | Slave14 EMD-4 Name | RW | 32 bytes
36384 | Slave14 EMD-5 Name | RW | 32 bytes
36400 | Slave14 EMD-6 Name | RW | 32 bytes
36416 | Slave14 EMD-7 Name | RW | 32 bytes
36432 | Slave14 EMD-8 Name | RW | 32 bytes
36448 | Slave15 EMD-1 Name | RW | 32 bytes
36464 | Slave15 EMD-2 Name | RW | 32 bytes
36480 | Slave15 EMD-3 Name | RW | 32 bytes
36496 | Slave15 EMD-4 Name | RW | 32 bytes
36512 | Slave15 EMD-5 Name | RW | 32 bytes
36528 | Slave15 EMD-6 Name | RW | 32 bytes
36544 | Slave15 EMD-7 Name | RW | 32 bytes
36560 | Slave15 EMD-8 Name | RW | 32 bytes
36576 | Master EMD-1 Temperature Name | RW | 32 bytes
36592 | Master EMD-2 Temperature Name | RW | 32 bytes
36608 | Master EMD-3 Temperature Name | RW | 32 bytes
36624 | Master EMD-4 Temperature Name | RW | 32 bytes
36640 | Master EMD-5 Temperature Name | RW | 32 bytes
36656 | Master EMD-6 Temperature Name | RW | 32 bytes
36672 | Master EMD-7 Temperature Name | RW | 32 bytes
36688 | Master EMD-8 Temperature Name | RW | 32 bytes
36704 | Slave01 EMD-1 Temperature Name | RW | 32 bytes
36720 | Slave01 EMD-2 Temperature Name | RW | 32 bytes
36736 | Slave01 EMD-3 Temperature Name | RW | 32 bytes
36752 | Slave01 EMD-4 Temperature Name | RW | 32 bytes
36768 | Slave01 EMD-5 Temperature Name | RW | 32 bytes
36784 | Slave01 EMD-6 Temperature Name | RW | 32 bytes
36800 | Slave01 EMD-7 Temperature Name | RW | 32 bytes
36816 | Slave01 EMD-8 Temperature Name | RW | 32 bytes
36832 | Slave02 EMD-1 Temperature Name | RW | 32 bytes
36848 | Slave02 EMD-2 Temperature Name | RW | 32 bytes
36864 | Slave02 EMD-3 Temperature Name | RW | 32 bytes
36880 | Slave02 EMD-4 Temperature Name | RW | 32 bytes
36896 | Slave02 EMD-5 Temperature Name | RW | 32 bytes
36912 | Slave02 EMD-6 Temperature Name | RW | 32 bytes
36928 | Slave02 EMD-7 Temperature Name | RW | 32 bytes
36944 | Slave02 EMD-8 Temperature Name | RW | 32 bytes
36960 | Slave03 EMD-1 Temperature Name | RW | 32 bytes
36976 | Slave03 EMD-2 Temperature Name | RW | 32 bytes
36992 | Slave03 EMD-3 Temperature Name | RW | 32 bytes
37008 | Slave03 EMD-4 Temperature Name | RW | 32 bytes
37024 | Slave03 EMD-5 Temperature Name | RW | 32 bytes
37040 | Slave03 EMD-6 Temperature Name | RW | 32 bytes
37056 | Slave03 EMD-7 Temperature Name | RW | 32 bytes
37072 | Slave03 EMD-8 Temperature Name | RW | 32 bytes
37088 | Slave04 EMD-1 Temperature Name | RW | 32 bytes
37104 | Slave04 EMD-2 Temperature Name | RW | 32 bytes
37120 | Slave04 EMD-3 Temperature Name | RW | 32 bytes
37136 | Slave04 EMD-4 Temperature Name | RW | 32 bytes
37152 | Slave04 EMD-5 Temperature Name | RW | 32 bytes
37168 | Slave04 EMD-6 Temperature Name | RW | 32 bytes
37184 | Slave04 EMD-7 Temperature Name | RW | 32 bytes
37200 | Slave04 EMD-8 Temperature Name | RW | 32 bytes
37216 | Slave05 EMD-1 Temperature Name | RW | 32 bytes
37232 | Slave05 EMD-2 Temperature Name | RW | 32 bytes
37248 | Slave05 EMD-3 Temperature Name | RW | 32 bytes
37264 | Slave05 EMD-4 Temperature Name | RW | 32 bytes
37280 | Slave05 EMD-5 Temperature Name | RW | 32 bytes
37296 | Slave05 EMD-6 Temperature Name | RW | 32 bytes
37312 | Slave05 EMD-7 Temperature Name | RW | 32 bytes
37328 | Slave05 EMD-8 Temperature Name | RW | 32 bytes
37344 | Slave06 EMD-1 Temperature Name | RW | 32 bytes
37360 | Slave06 EMD-2 Temperature Name | RW | 32 bytes
37376 | Slave06 EMD-3 Temperature Name | RW | 32 bytes
37392 | Slave06 EMD-4 Temperature Name | RW | 32 bytes
37408 | Slave06 EMD-5 Temperature Name | RW | 32 bytes
37424 | Slave06 EMD-6 Temperature Name | RW | 32 bytes
37440 | Slave06 EMD-7 Temperature Name | RW | 32 bytes
37456 | Slave06 EMD-8 Temperature Name | RW | 32 bytes
37472 | Slave07 EMD-1 Temperature Name | RW | 32 bytes
37488 | Slave07 EMD-2 Temperature Name | RW | 32 bytes
37504 | Slave07 EMD-3 Temperature Name | RW | 32 bytes
37520 | Slave07 EMD-4 Temperature Name | RW | 32 bytes
37536 | Slave07 EMD-5 Temperature Name | RW | 32 bytes
37552 | Slave07 EMD-6 Temperature Name | RW | 32 bytes
37568 | Slave07 EMD-7 Temperature Name | RW | 32 bytes
37584 | Slave07 EMD-8 Temperature Name | RW | 32 bytes
37600 | Slave08 EMD-1 Temperature Name | RW | 32 bytes
37616 | Slave08 EMD-2 Temperature Name | RW | 32 bytes
37632 | Slave08 EMD-3 Temperature Name | RW | 32 bytes
37648 | Slave08 EMD-4 Temperature Name | RW | 32 bytes
37664 | Slave08 EMD-5 Temperature Name | RW | 32 bytes
37680 | Slave08 EMD-6 Temperature Name | RW | 32 bytes
37696 | Slave08 EMD-7 Temperature Name | RW | 32 bytes
37712 | Slave08 EMD-8 Temperature Name | RW | 32 bytes
37728 | Slave09 EMD-1 Temperature Name | RW | 32 bytes
37744 | Slave09 EMD-2 Temperature Name | RW | 32 bytes
37760 | Slave09 EMD-3 Temperature Name | RW | 32 bytes
37776 | Slave09 EMD-4 Temperature Name | RW | 32 bytes
37792 | Slave09 EMD-5 Temperature Name | RW | 32 bytes
37808 | Slave09 EMD-6 Temperature Name | RW | 32 bytes
37824 | Slave09 EMD-7 Temperature Name | RW | 32 bytes
37840 | Slave09 EMD-8 Temperature Name | RW | 32 bytes
37856 | Slave10 EMD-1 Temperature Name | RW | 32 bytes
37872 | Slave10 EMD-2 Temperature Name | RW | 32 bytes
37888 | Slave10 EMD-3 Temperature Name | RW | 32 bytes
37904 | Slave10 EMD-4 Temperature Name | RW | 32 bytes
37920 | Slave10 EMD-5 Temperature Name | RW | 32 bytes
37936 | Slave10 EMD-6 Temperature Name | RW | 32 bytes
37952 | Slave10 EMD-7 Temperature Name | RW | 32 bytes
37968 | Slave10 EMD-8 Temperature Name | RW | 32 bytes
37984 | Slave11 EMD-1 Temperature Name | RW | 32 bytes
38000 | Slave11 EMD-2 Temperature Name | RW | 32 bytes
38016 | Slave11 EMD-3 Temperature Name | RW | 32 bytes
38032 | Slave11 EMD-4 Temperature Name | RW | 32 bytes
38048 | Slave11 EMD-5 Temperature Name | RW | 32 bytes
38064 | Slave11 EMD-6 Temperature Name | RW | 32 bytes
38080 | Slave11 EMD-7 Temperature Name | RW | 32 bytes
38096 | Slave11 EMD-8 Temperature Name | RW | 32 bytes
38112 | Slave12 EMD-1 Temperature Name | RW | 32 bytes
38128 | Slave12 EMD-2 Temperature Name | RW | 32 bytes
38144 | Slave12 EMD-3 Temperature Name | RW | 32 bytes
38160 | Slave12 EMD-4 Temperature Name | RW | 32 bytes
38176 | Slave12 EMD-5 Temperature Name | RW | 32 bytes
38192 | Slave12 EMD-6 Temperature Name | RW | 32 bytes
38208 | Slave12 EMD-7 Temperature Name | RW | 32 bytes
38224 | Slave12 EMD-8 Temperature Name | RW | 32 bytes
38240 | Slave13 EMD-1 Temperature Name | RW | 32 bytes
38256 | Slave13 EMD-2 Temperature Name | RW | 32 bytes
38272 | Slave13 EMD-3 Temperature Name | RW | 32 bytes
38288 | Slave13 EMD-4 Temperature Name | RW | 32 bytes
38304 | Slave13 EMD-5 Temperature Name | RW | 32 bytes
38320 | Slave13 EMD-6 Temperature Name | RW | 32 bytes
38336 | Slave13 EMD-7 Temperature Name | RW | 32 bytes
38352 | Slave13 EMD-8 Temperature Name | RW | 32 bytes
38368 | Slave14 EMD-1 Temperature Name | RW | 32 bytes
38384 | Slave14 EMD-2 Temperature Name | RW | 32 bytes
38400 | Slave14 EMD-3 Temperature Name | RW | 32 bytes
38416 | Slave14 EMD-4 Temperature Name | RW | 32 bytes
38432 | Slave14 EMD-5 Temperature Name | RW | 32 bytes
38448 | Slave14 EMD-6 Temperature Name | RW | 32 bytes
38464 | Slave14 EMD-7 Temperature Name | RW | 32 bytes
38480 | Slave14 EMD-8 Temperature Name | RW | 32 bytes
38496 | Slave15 EMD-1 Temperature Name | RW | 32 bytes
38512 | Slave15 EMD-2 Temperature Name | RW | 32 bytes
38528 | Slave15 EMD-3 Temperature Name | RW | 32 bytes
38544 | Slave15 EMD-4 Temperature Name | RW | 32 bytes
38560 | Slave15 EMD-5 Temperature Name | RW | 32 bytes
38576 | Slave15 EMD-6 Temperature Name | RW | 32 bytes
38592 | Slave15 EMD-7 Temperature Name | RW | 32 bytes
38608 | Slave15 EMD-8 Temperature Name | RW | 32 bytes
38624 | Master EMD-1 Humidity Name | RW | 32 bytes
38640 | Master EMD-2 Humidity Name | RW | 32 bytes
38656 | Master EMD-3 Humidity Name | RW | 32 bytes
38672 | Master EMD-4 Humidity Name | RW | 32 bytes
38688 | Master EMD-5 Humidity Name | RW | 32 bytes
38704 | Master EMD-6 Humidity Name | RW | 32 bytes
38720 | Master EMD-7 Humidity Name | RW | 32 bytes
38736 | Master EMD-8 Humidity Name | RW | 32 bytes
38752 | Slave01 EMD-1 Humidity Name | RW | 32 bytes
38768 | Slave01 EMD-2 Humidity Name | RW | 32 bytes
38784 | Slave01 EMD-3 Humidity Name | RW | 32 bytes
38800 | Slave01 EMD-4 Humidity Name | RW | 32 bytes
38816 | Slave01 EMD-5 Humidity Name | RW | 32 bytes
38832 | Slave01 EMD-6 Humidity Name | RW | 32 bytes
38848 | Slave01 EMD-7 Humidity Name | RW | 32 bytes
38864 | Slave01 EMD-8 Humidity Name | RW | 32 bytes
38880 | Slave02 EMD-1 Humidity Name | RW | 32 bytes
38896 | Slave02 EMD-2 Humidity Name | RW | 32 bytes
38912 | Slave02 EMD-3 Humidity Name | RW | 32 bytes
38928 | Slave02 EMD-4 Humidity Name | RW | 32 bytes
38944 | Slave02 EMD-5 Humidity Name | RW | 32 bytes
38960 | Slave02 EMD-6 Humidity Name | RW | 32 bytes
38976 | Slave02 EMD-7 Humidity Name | RW | 32 bytes
38992 | Slave02 EMD-8 Humidity Name | RW | 32 bytes
39008 | Slave03 EMD-1 Humidity Name | RW | 32 bytes
39024 | Slave03 EMD-2 Humidity Name | RW | 32 bytes
39040 | Slave03 EMD-3 Humidity Name | RW | 32 bytes
39056 | Slave03 EMD-4 Humidity Name | RW | 32 bytes
39072 | Slave03 EMD-5 Humidity Name | RW | 32 bytes
39088 | Slave03 EMD-6 Humidity Name | RW | 32 bytes
39104 | Slave03 EMD-7 Humidity Name | RW | 32 bytes
39120 | Slave03 EMD-8 Humidity Name | RW | 32 bytes
39136 | Slave04 EMD-1 Humidity Name | RW | 32 bytes
39152 | Slave04 EMD-2 Humidity Name | RW | 32 bytes
39168 | Slave04 EMD-3 Humidity Name | RW | 32 bytes
39184 | Slave04 EMD-4 Humidity Name | RW | 32 bytes
39200 | Slave04 EMD-5 Humidity Name | RW | 32 bytes
39216 | Slave04 EMD-6 Humidity Name | RW | 32 bytes
39232 | Slave04 EMD-7 Humidity Name | RW | 32 bytes
39248 | Slave04 EMD-8 Humidity Name | RW | 32 bytes
39264 | Slave05 EMD-1 Humidity Name | RW | 32 bytes
39280 | Slave05 EMD-2 Humidity Name | RW | 32 bytes
39296 | Slave05 EMD-3 Humidity Name | RW | 32 bytes
39312 | Slave05 EMD-4 Humidity Name | RW | 32 bytes
39328 | Slave05 EMD-5 Humidity Name | RW | 32 bytes
39344 | Slave05 EMD-6 Humidity Name | RW | 32 bytes
39360 | Slave05 EMD-7 Humidity Name | RW | 32 bytes
39376 | Slave05 EMD-8 Humidity Name | RW | 32 bytes
39392 | Slave06 EMD-1 Humidity Name | RW | 32 bytes
39408 | Slave06 EMD-2 Humidity Name | RW | 32 bytes
39424 | Slave06 EMD-3 Humidity Name | RW | 32 bytes
39440 | Slave06 EMD-4 Humidity Name | RW | 32 bytes
39456 | Slave06 EMD-5 Humidity Name | RW | 32 bytes
39472 | Slave06 EMD-6 Humidity Name | RW | 32 bytes
39488 | Slave06 EMD-7 Humidity Name | RW | 32 bytes
39504 | Slave06 EMD-8 Humidity Name | RW | 32 bytes
39520 | Slave07 EMD-1 Humidity Name | RW | 32 bytes
39536 | Slave07 EMD-2 Humidity Name | RW | 32 bytes
39552 | Slave07 EMD-3 Humidity Name | RW | 32 bytes
39568 | Slave07 EMD-4 Humidity Name | RW | 32 bytes
39584 | Slave07 EMD-5 Humidity Name | RW | 32 bytes
39600 | Slave07 EMD-6 Humidity Name | RW | 32 bytes
39616 | Slave07 EMD-7 Humidity Name | RW | 32 bytes
39632 | Slave07 EMD-8 Humidity Name | RW | 32 bytes
39648 | Slave08 EMD-1 Humidity Name | RW | 32 bytes
39664 | Slave08 EMD-2 Humidity Name | RW | 32 bytes
39680 | Slave08 EMD-3 Humidity Name | RW | 32 bytes
39696 | Slave08 EMD-4 Humidity Name | RW | 32 bytes
39712 | Slave08 EMD-5 Humidity Name | RW | 32 bytes
39728 | Slave08 EMD-6 Humidity Name | RW | 32 bytes
39744 | Slave08 EMD-7 Humidity Name | RW | 32 bytes
39760 | Slave08 EMD-8 Humidity Name | RW | 32 bytes
39776 | Slave09 EMD-1 Humidity Name | RW | 32 bytes
39792 | Slave09 EMD-2 Humidity Name | RW | 32 bytes
39808 | Slave09 EMD-3 Humidity Name | RW | 32 bytes
39824 | Slave09 EMD-4 Humidity Name | RW | 32 bytes
39840 | Slave09 EMD-5 Humidity Name | RW | 32 bytes
39856 | Slave09 EMD-6 Humidity Name | RW | 32 bytes
39872 | Slave09 EMD-7 Humidity Name | RW | 32 bytes
39888 | Slave09 EMD-8 Humidity Name | RW | 32 bytes
39904 | Slave10 EMD-1 Humidity Name | RW | 32 bytes
39920 | Slave10 EMD-2 Humidity Name | RW | 32 bytes
39936 | Slave10 EMD-3 Humidity Name | RW | 32 bytes
39952 | Slave10 EMD-4 Humidity Name | RW | 32 bytes
39968 | Slave10 EMD-5 Humidity Name | RW | 32 bytes
39984 | Slave10 EMD-6 Humidity Name | RW | 32 bytes
40000 | Slave10 EMD-7 Humidity Name | RW | 32 bytes
40016 | Slave10 EMD-8 Humidity Name | RW | 32 bytes
40032 | Slave11 EMD-1 Humidity Name | RW | 32 bytes
40048 | Slave11 EMD-2 Humidity Name | RW | 32 bytes
40064 | Slave11 EMD-3 Humidity Name | RW | 32 bytes
40080 | Slave11 EMD-4 Humidity Name | RW | 32 bytes
40096 | Slave11 EMD-5 Humidity Name | RW | 32 bytes
40112 | Slave11 EMD-6 Humidity Name | RW | 32 bytes
40128 | Slave11 EMD-7 Humidity Name | RW | 32 bytes
40144 | Slave11 EMD-8 Humidity Name | RW | 32 bytes
40160 | Slave12 EMD-1 Humidity Name | RW | 32 bytes
40176 | Slave12 EMD-2 Humidity Name | RW | 32 bytes
40192 | Slave12 EMD-3 Humidity Name | RW | 32 bytes
40208 | Slave12 EMD-4 Humidity Name | RW | 32 bytes
40224 | Slave12 EMD-5 Humidity Name | RW | 32 bytes
40240 | Slave12 EMD-6 Humidity Name | RW | 32 bytes
40256 | Slave12 EMD-7 Humidity Name | RW | 32 bytes
40272 | Slave12 EMD-8 Humidity Name | RW | 32 bytes
40288 | Slave13 EMD-1 Humidity Name | RW | 32 bytes
40304 | Slave13 EMD-2 Humidity Name | RW | 32 bytes
40320 | Slave13 EMD-3 Humidity Name | RW | 32 bytes
40336 | Slave13 EMD-4 Humidity Name | RW | 32 bytes
40352 | Slave13 EMD-5 Humidity Name | RW | 32 bytes
40368 | Slave13 EMD-6 Humidity Name | RW | 32 bytes
40384 | Slave13 EMD-7 Humidity Name | RW | 32 bytes
40400 | Slave13 EMD-8 Humidity Name | RW | 32 bytes
40416 | Slave14 EMD-1 Humidity Name | RW | 32 bytes
40432 | Slave14 EMD-2 Humidity Name | RW | 32 bytes
40448 | Slave14 EMD-3 Humidity Name | RW | 32 bytes
40464 | Slave14 EMD-4 Humidity Name | RW | 32 bytes
40480 | Slave14 EMD-5 Humidity Name | RW | 32 bytes
40496 | Slave14 EMD-6 Humidity Name | RW | 32 bytes
40512 | Slave14 EMD-7 Humidity Name | RW | 32 bytes
40528 | Slave14 EMD-8 Humidity Name | RW | 32 bytes
40544 | Slave15 EMD-1 Humidity Name | RW | 32 bytes
40560 | Slave15 EMD-2 Humidity Name | RW | 32 bytes
40576 | Slave15 EMD-3 Humidity Name | RW | 32 bytes
40592 | Slave15 EMD-4 Humidity Name | RW | 32 bytes
40608 | Slave15 EMD-5 Humidity Name | RW | 32 bytes
40624 | Slave15 EMD-6 Humidity Name | RW | 32 bytes
40640 | Slave15 EMD-7 Humidity Name | RW | 32 bytes
40656 | Slave15 EMD-8 Humidity Name | RW | 32 bytes
40672 | Master EMD-1 Alarm1 Name | RW | 32 bytes
40688 | Master EMD-2 Alarm1 Name | RW | 32 bytes
40704 | Master EMD-3 Alarm1 Name | RW | 32 bytes
40720 | Master EMD-4 Alarm1 Name | RW | 32 bytes
40736 | Master EMD-5 Alarm1 Name | RW | 32 bytes
40752 | Master EMD-6 Alarm1 Name | RW | 32 bytes
40768 | Master EMD-7 Alarm1 Name | RW | 32 bytes
40784 | Master EMD-8 Alarm1 Name | RW | 32 bytes
40800 | Slave01 EMD-1 Alarm1 Name | RW | 32 bytes
40816 | Slave01 EMD-2 Alarm1 Name | RW | 32 bytes
40832 | Slave01 EMD-3 Alarm1 Name | RW | 32 bytes
40848 | Slave01 EMD-4 Alarm1 Name | RW | 32 bytes
40864 | Slave01 EMD-5 Alarm1 Name | RW | 32 bytes
40880 | Slave01 EMD-6 Alarm1 Name | RW | 32 bytes
40896 | Slave01 EMD-7 Alarm1 Name | RW | 32 bytes
40912 | Slave01 EMD-8 Alarm1 Name | RW | 32 bytes
40928 | Slave02 EMD-1 Alarm1 Name | RW | 32 bytes
40944 | Slave02 EMD-2 Alarm1 Name | RW | 32 bytes
40960 | Slave02 EMD-3 Alarm1 Name | RW | 32 bytes
40976 | Slave02 EMD-4 Alarm1 Name | RW | 32 bytes
40992 | Slave02 EMD-5 Alarm1 Name | RW | 32 bytes
41008 | Slave02 EMD-6 Alarm1 Name | RW | 32 bytes
41024 | Slave02 EMD-7 Alarm1 Name | RW | 32 bytes
41040 | Slave02 EMD-8 Alarm1 Name | RW | 32 bytes
41056 | Slave03 EMD-1 Alarm1 Name | RW | 32 bytes
41072 | Slave03 EMD-2 Alarm1 Name | RW | 32 bytes
41088 | Slave03 EMD-3 Alarm1 Name | RW | 32 bytes
41104 | Slave03 EMD-4 Alarm1 Name | RW | 32 bytes
41120 | Slave03 EMD-5 Alarm1 Name | RW | 32 bytes
41136 | Slave03 EMD-6 Alarm1 Name | RW | 32 bytes
41152 | Slave03 EMD-7 Alarm1 Name | RW | 32 bytes
41168 | Slave03 EMD-8 Alarm1 Name | RW | 32 bytes
41184 | Slave04 EMD-1 Alarm1 Name | RW | 32 bytes
41200 | Slave04 EMD-2 Alarm1 Name | RW | 32 bytes
41216 | Slave04 EMD-3 Alarm1 Name | RW | 32 bytes
41232 | Slave04 EMD-4 Alarm1 Name | RW | 32 bytes
41248 | Slave04 EMD-5 Alarm1 Name | RW | 32 bytes
41264 | Slave04 EMD-6 Alarm1 Name | RW | 32 bytes
41280 | Slave04 EMD-7 Alarm1 Name | RW | 32 bytes
41296 | Slave04 EMD-8 Alarm1 Name | RW | 32 bytes
41312 | Slave05 EMD-1 Alarm1 Name | RW | 32 bytes
41328 | Slave05 EMD-2 Alarm1 Name | RW | 32 bytes
41344 | Slave05 EMD-3 Alarm1 Name | RW | 32 bytes
41360 | Slave05 EMD-4 Alarm1 Name | RW | 32 bytes
41376 | Slave05 EMD-5 Alarm1 Name | RW | 32 bytes
41392 | Slave05 EMD-6 Alarm1 Name | RW | 32 bytes
41408 | Slave05 EMD-7 Alarm1 Name | RW | 32 bytes
41424 | Slave05 EMD-8 Alarm1 Name | RW | 32 bytes
41440 | Slave06 EMD-1 Alarm1 Name | RW | 32 bytes
41456 | Slave06 EMD-2 Alarm1 Name | RW | 32 bytes
41472 | Slave06 EMD-3 Alarm1 Name | RW | 32 bytes
41488 | Slave06 EMD-4 Alarm1 Name | RW | 32 bytes
41504 | Slave06 EMD-5 Alarm1 Name | RW | 32 bytes
41520 | Slave06 EMD-6 Alarm1 Name | RW | 32 bytes
41536 | Slave06 EMD-7 Alarm1 Name | RW | 32 bytes
41552 | Slave06 EMD-8 Alarm1 Name | RW | 32 bytes
41568 | Slave07 EMD-1 Alarm1 Name | RW | 32 bytes
41584 | Slave07 EMD-2 Alarm1 Name | RW | 32 bytes
41600 | Slave07 EMD-3 Alarm1 Name | RW | 32 bytes
41616 | Slave07 EMD-4 Alarm1 Name | RW | 32 bytes
41632 | Slave07 EMD-5 Alarm1 Name | RW | 32 bytes
41648 | Slave07 EMD-6 Alarm1 Name | RW | 32 bytes
41664 | Slave07 EMD-7 Alarm1 Name | RW | 32 bytes
41680 | Slave07 EMD-8 Alarm1 Name | RW | 32 bytes
41696 | Slave08 EMD-1 Alarm1 Name | RW | 32 bytes
41712 | Slave08 EMD-2 Alarm1 Name | RW | 32 bytes
41728 | Slave08 EMD-3 Alarm1 Name | RW | 32 bytes
41744 | Slave08 EMD-4 Alarm1 Name | RW | 32 bytes
41760 | Slave08 EMD-5 Alarm1 Name | RW | 32 bytes
41776 | Slave08 EMD-6 Alarm1 Name | RW | 32 bytes
41792 | Slave08 EMD-7 Alarm1 Name | RW | 32 bytes
41808 | Slave08 EMD-8 Alarm1 Name | RW | 32 bytes
41824 | Slave09 EMD-1 Alarm1 Name | RW | 32 bytes
41840 | Slave09 EMD-2 Alarm1 Name | RW | 32 bytes
41856 | Slave09 EMD-3 Alarm1 Name | RW | 32 bytes
41872 | Slave09 EMD-4 Alarm1 Name | RW | 32 bytes
41888 | Slave09 EMD-5 Alarm1 Name | RW | 32 bytes
41904 | Slave09 EMD-6 Alarm1 Name | RW | 32 bytes
41920 | Slave09 EMD-7 Alarm1 Name | RW | 32 bytes
41936 | Slave09 EMD-8 Alarm1 Name | RW | 32 bytes
41952 | Slave10 EMD-1 Alarm1 Name | RW | 32 bytes
41968 | Slave10 EMD-2 Alarm1 Name | RW | 32 bytes
41984 | Slave10 EMD-3 Alarm1 Name | RW | 32 bytes
42000 | Slave10 EMD-4 Alarm1 Name | RW | 32 bytes
42016 | Slave10 EMD-5 Alarm1 Name | RW | 32 bytes
42032 | Slave10 EMD-6 Alarm1 Name | RW | 32 bytes
42048 | Slave10 EMD-7 Alarm1 Name | RW | 32 bytes
42064 | Slave10 EMD-8 Alarm1 Name | RW | 32 bytes
42080 | Slave11 EMD-1 Alarm1 Name | RW | 32 bytes
42096 | Slave11 EMD-2 Alarm1 Name | RW | 32 bytes
42112 | Slave11 EMD-3 Alarm1 Name | RW | 32 bytes
42128 | Slave11 EMD-4 Alarm1 Name | RW | 32 bytes
42144 | Slave11 EMD-5 Alarm1 Name | RW | 32 bytes
42160 | Slave11 EMD-6 Alarm1 Name | RW | 32 bytes
42176 | Slave11 EMD-7 Alarm1 Name | RW | 32 bytes
42192 | Slave11 EMD-8 Alarm1 Name | RW | 32 bytes
42208 | Slave12 EMD-1 Alarm1 Name | RW | 32 bytes
42224 | Slave12 EMD-2 Alarm1 Name | RW | 32 bytes
42240 | Slave12 EMD-3 Alarm1 Name | RW | 32 bytes
42256 | Slave12 EMD-4 Alarm1 Name | RW | 32 bytes
42272 | Slave12 EMD-5 Alarm1 Name | RW | 32 bytes
42288 | Slave12 EMD-6 Alarm1 Name | RW | 32 bytes
42304 | Slave12 EMD-7 Alarm1 Name | RW | 32 bytes
42320 | Slave12 EMD-8 Alarm1 Name | RW | 32 bytes
42336 | Slave13 EMD-1 Alarm1 Name | RW | 32 bytes
42352 | Slave13 EMD-2 Alarm1 Name | RW | 32 bytes
42368 | Slave13 EMD-3 Alarm1 Name | RW | 32 bytes
42384 | Slave13 EMD-4 Alarm1 Name | RW | 32 bytes
42400 | Slave13 EMD-5 Alarm1 Name | RW | 32 bytes
42416 | Slave13 EMD-6 Alarm1 Name | RW | 32 bytes
42432 | Slave13 EMD-7 Alarm1 Name | RW | 32 bytes
42448 | Slave13 EMD-8 Alarm1 Name | RW | 32 bytes
42464 | Slave14 EMD-1 Alarm1 Name | RW | 32 bytes
42480 | Slave14 EMD-2 Alarm1 Name | RW | 32 bytes
42496 | Slave14 EMD-3 Alarm1 Name | RW | 32 bytes
42512 | Slave14 EMD-4 Alarm1 Name | RW | 32 bytes
42528 | Slave14 EMD-5 Alarm1 Name | RW | 32 bytes
42544 | Slave14 EMD-6 Alarm1 Name | RW | 32 bytes
42560 | Slave14 EMD-7 Alarm1 Name | RW | 32 bytes
42576 | Slave14 EMD-8 Alarm1 Name | RW | 32 bytes
42592 | Slave15 EMD-1 Alarm1 Name | RW | 32 bytes
42608 | Slave15 EMD-2 Alarm1 Name | RW | 32 bytes
42624 | Slave15 EMD-3 Alarm1 Name | RW | 32 bytes
42640 | Slave15 EMD-4 Alarm1 Name | RW | 32 bytes
42656 | Slave15 EMD-5 Alarm1 Name | RW | 32 bytes
42672 | Slave15 EMD-6 Alarm1 Name | RW | 32 bytes
42688 | Slave15 EMD-7 Alarm1 Name | RW | 32 bytes
42704 | Slave15 EMD-8 Alarm1 Name | RW | 32 bytes
42720 | Master EMD-1 Alarm2 Name | RW | 32 bytes
42736 | Master EMD-2 Alarm2 Name | RW | 32 bytes
42752 | Master EMD-3 Alarm2 Name | RW | 32 bytes
42768 | Master EMD-4 Alarm2 Name | RW | 32 bytes
42784 | Master EMD-5 Alarm2 Name | RW | 32 bytes
42800 | Master EMD-6 Alarm2 Name | RW | 32 bytes
42816 | Master EMD-7 Alarm2 Name | RW | 32 bytes
42832 | Master EMD-8 Alarm2 Name | RW | 32 bytes
42848 | Slave01 EMD-1 Alarm2 Name | RW | 32 bytes
42864 | Slave01 EMD-2 Alarm2 Name | RW | 32 bytes
42880 | Slave01 EMD-3 Alarm2 Name | RW | 32 bytes
42896 | Slave01 EMD-4 Alarm2 Name | RW | 32 bytes
42912 | Slave01 EMD-5 Alarm2 Name | RW | 32 bytes
42928 | Slave01 EMD-6 Alarm2 Name | RW | 32 bytes
42944 | Slave01 EMD-7 Alarm2 Name | RW | 32 bytes
42960 | Slave01 EMD-8 Alarm2 Name | RW | 32 bytes
42976 | Slave02 EMD-1 Alarm2 Name | RW | 32 bytes
42992 | Slave02 EMD-2 Alarm2 Name | RW | 32 bytes
43008 | Slave02 EMD-3 Alarm2 Name | RW | 32 bytes
43024 | Slave02 EMD-4 Alarm2 Name | RW | 32 bytes
43040 | Slave02 EMD-5 Alarm2 Name | RW | 32 bytes
43056 | Slave02 EMD-6 Alarm2 Name | RW | 32 bytes
43072 | Slave02 EMD-7 Alarm2 Name | RW | 32 bytes
43088 | Slave02 EMD-8 Alarm2 Name | RW | 32 bytes
43104 | Slave03 EMD-1 Alarm2 Name | RW | 32 bytes
43120 | Slave03 EMD-2 Alarm2 Name | RW | 32 bytes
43136 | Slave03 EMD-3 Alarm2 Name | RW | 32 bytes
43152 | Slave03 EMD-4 Alarm2 Name | RW | 32 bytes
43168 | Slave03 EMD-5 Alarm2 Name | RW | 32 bytes
43184 | Slave03 EMD-6 Alarm2 Name | RW | 32 bytes
43200 | Slave03 EMD-7 Alarm2 Name | RW | 32 bytes
43216 | Slave03 EMD-8 Alarm2 Name | RW | 32 bytes
43232 | Slave04 EMD-1 Alarm2 Name | RW | 32 bytes
43248 | Slave04 EMD-2 Alarm2 Name | RW | 32 bytes
43264 | Slave04 EMD-3 Alarm2 Name | RW | 32 bytes
43280 | Slave04 EMD-4 Alarm2 Name | RW | 32 bytes
43296 | Slave04 EMD-5 Alarm2 Name | RW | 32 bytes
43312 | Slave04 EMD-6 Alarm2 Name | RW | 32 bytes
43328 | Slave04 EMD-7 Alarm2 Name | RW | 32 bytes
43344 | Slave04 EMD-8 Alarm2 Name | RW | 32 bytes
43360 | Slave05 EMD-1 Alarm2 Name | RW | 32 bytes
43376 | Slave05 EMD-2 Alarm2 Name | RW | 32 bytes
43392 | Slave05 EMD-3 Alarm2 Name | RW | 32 bytes
43408 | Slave05 EMD-4 Alarm2 Name | RW | 32 bytes
43424 | Slave05 EMD-5 Alarm2 Name | RW | 32 bytes
43440 | Slave05 EMD-6 Alarm2 Name | RW | 32 bytes
43456 | Slave05 EMD-7 Alarm2 Name | RW | 32 bytes
43472 | Slave05 EMD-8 Alarm2 Name | RW | 32 bytes
43488 | Slave06 EMD-1 Alarm2 Name | RW | 32 bytes
43504 | Slave06 EMD-2 Alarm2 Name | RW | 32 bytes
43520 | Slave06 EMD-3 Alarm2 Name | RW | 32 bytes
43536 | Slave06 EMD-4 Alarm2 Name | RW | 32 bytes
43552 | Slave06 EMD-5 Alarm2 Name | RW | 32 bytes
43568 | Slave06 EMD-6 Alarm2 Name | RW | 32 bytes
43584 | Slave06 EMD-7 Alarm2 Name | RW | 32 bytes
43600 | Slave06 EMD-8 Alarm2 Name | RW | 32 bytes
43616 | Slave07 EMD-1 Alarm2 Name | RW | 32 bytes
43632 | Slave07 EMD-2 Alarm2 Name | RW | 32 bytes
43648 | Slave07 EMD-3 Alarm2 Name | RW | 32 bytes
43664 | Slave07 EMD-4 Alarm2 Name | RW | 32 bytes
43680 | Slave07 EMD-5 Alarm2 Name | RW | 32 bytes
43696 | Slave07 EMD-6 Alarm2 Name | RW | 32 bytes
43712 | Slave07 EMD-7 Alarm2 Name | RW | 32 bytes
43728 | Slave07 EMD-8 Alarm2 Name | RW | 32 bytes
43744 | Slave08 EMD-1 Alarm2 Name | RW | 32 bytes
43760 | Slave08 EMD-2 Alarm2 Name | RW | 32 bytes
43776 | Slave08 EMD-3 Alarm2 Name | RW | 32 bytes
43792 | Slave08 EMD-4 Alarm2 Name | RW | 32 bytes
43808 | Slave08 EMD-5 Alarm2 Name | RW | 32 bytes
43824 | Slave08 EMD-6 Alarm2 Name | RW | 32 bytes
43840 | Slave08 EMD-7 Alarm2 Name | RW | 32 bytes
43856 | Slave08 EMD-8 Alarm2 Name | RW | 32 bytes
43872 | Slave09 EMD-1 Alarm2 Name | RW | 32 bytes
43888 | Slave09 EMD-2 Alarm2 Name | RW | 32 bytes
43904 | Slave09 EMD-3 Alarm2 Name | RW | 32 bytes
43920 | Slave09 EMD-4 Alarm2 Name | RW | 32 bytes
43936 | Slave09 EMD-5 Alarm2 Name | RW | 32 bytes
43952 | Slave09 EMD-6 Alarm2 Name | RW | 32 bytes
43968 | Slave09 EMD-7 Alarm2 Name | RW | 32 bytes
43984 | Slave09 EMD-8 Alarm2 Name | RW | 32 bytes
44000 | Slave10 EMD-1 Alarm2 Name | RW | 32 bytes
44016 | Slave10 EMD-2 Alarm2 Name | RW | 32 bytes
44032 | Slave10 EMD-3 Alarm2 Name | RW | 32 bytes
44048 | Slave10 EMD-4 Alarm2 Name | RW | 32 bytes
44064 | Slave10 EMD-5 Alarm2 Name | RW | 32 bytes
44080 | Slave10 EMD-6 Alarm2 Name | RW | 32 bytes
44096 | Slave10 EMD-7 Alarm2 Name | RW | 32 bytes
44112 | Slave10 EMD-8 Alarm2 Name | RW | 32 bytes
44128 | Slave11 EMD-1 Alarm2 Name | RW | 32 bytes
44144 | Slave11 EMD-2 Alarm2 Name | RW | 32 bytes
44160 | Slave11 EMD-3 Alarm2 Name | RW | 32 bytes
44176 | Slave11 EMD-4 Alarm2 Name | RW | 32 bytes
44192 | Slave11 EMD-5 Alarm2 Name | RW | 32 bytes
44208 | Slave11 EMD-6 Alarm2 Name | RW | 32 bytes
44224 | Slave11 EMD-7 Alarm2 Name | RW | 32 bytes
44240 | Slave11 EMD-8 Alarm2 Name | RW | 32 bytes
44256 | Slave12 EMD-1 Alarm2 Name | RW | 32 bytes
44272 | Slave12 EMD-2 Alarm2 Name | RW | 32 bytes
44288 | Slave12 EMD-3 Alarm2 Name | RW | 32 bytes
44304 | Slave12 EMD-4 Alarm2 Name | RW | 32 bytes
44320 | Slave12 EMD-5 Alarm2 Name | RW | 32 bytes
44336 | Slave12 EMD-6 Alarm2 Name | RW | 32 bytes
44352 | Slave12 EMD-7 Alarm2 Name | RW | 32 bytes
44368 | Slave12 EMD-8 Alarm2 Name | RW | 32 bytes
44384 | Slave13 EMD-1 Alarm2 Name | RW | 32 bytes
44400 | Slave13 EMD-2 Alarm2 Name | RW | 32 bytes
44416 | Slave13 EMD-3 Alarm2 Name | RW | 32 bytes
44432 | Slave13 EMD-4 Alarm2 Name | RW | 32 bytes
44448 | Slave13 EMD-5 Alarm2 Name | RW | 32 bytes
44464 | Slave13 EMD-6 Alarm2 Name | RW | 32 bytes
44480 | Slave13 EMD-7 Alarm2 Name | RW | 32 bytes
44496 | Slave13 EMD-8 Alarm2 Name | RW | 32 bytes
44512 | Slave14 EMD-1 Alarm2 Name | RW | 32 bytes
44528 | Slave14 EMD-2 Alarm2 Name | RW | 32 bytes
44544 | Slave14 EMD-3 Alarm2 Name | RW | 32 bytes
44560 | Slave14 EMD-4 Alarm2 Name | RW | 32 bytes
44576 | Slave14 EMD-5 Alarm2 Name | RW | 32 bytes
44592 | Slave14 EMD-6 Alarm2 Name | RW | 32 bytes
44608 | Slave14 EMD-7 Alarm2 Name | RW | 32 bytes
44624 | Slave14 EMD-8 Alarm2 Name | RW | 32 bytes
44640 | Slave15 EMD-1 Alarm2 Name | RW | 32 bytes
44656 | Slave15 EMD-2 Alarm2 Name | RW | 32 bytes
44672 | Slave15 EMD-3 Alarm2 Name | RW | 32 bytes
44688 | Slave15 EMD-4 Alarm2 Name | RW | 32 bytes
44704 | Slave15 EMD-5 Alarm2 Name | RW | 32 bytes
44720 | Slave15 EMD-6 Alarm2 Name | RW | 32 bytes
44736 | Slave15 EMD-7 Alarm2 Name | RW | 32 bytes
44752 | Slave15 EMD-8 Alarm2 Name | RW | 32 bytes
44768 | Master PDU Status | RO | 2 bytes